## Assumptions & Sources
CV Low-Voltage Voltage-Drop Tool ¦ Assumptions & Sources
Parameter | Value
Copper temperature coefficient, α (1/°C) | 0.00393
Default conductor operating temperature (°C) | 90
Default voltage-drop limit | 3%
Default reactance, X (Ω/km) | 0.08
Reference temperature for Rdc (°C) | 20
Source / method | Reference | How used | Important limitation
Project source | สาย CV ที่ใช้ในโครงการ.xlsx | Selects the project CV cable types included in this tool. | The source contains cable descriptions only; it does not include electrical impedance data.
Manufacturer construction | https://www.pdcable.com/en/product-en/building-and-construction/cv-1-2/ | Confirms Phelps Dodge CV is 0.6/1 kV Cu/XLPE/PVC, IEC 60502-1, 1C/2C/3C/4C/5C. | Verify final catalogue/test values for the exact part number and installation arrangement.
Conductor Rdc | IEC 60228 Class 2 maximum DC resistance at 20°C | R20 is an editable design input; Rθ = R20 × [1 + α × (θ−20)]. | Values are conservative maximum conductor resistance, not a manufacturer AC-impedance certificate.
Voltage-drop method | IEC-style AC phasor approximation | 3Φ: √3·I·L·(Rcosφ+Xsinφ); 1Φ/DC 2-wire: 2·I·L·(Rcosφ+Xsinφ). | X and temperature must be checked against actual installation, grouping, spacing and cable formation.
Use / design note
This workbook checks voltage drop only. Confirm ampacity, derating, protective-device coordination, short-circuit withstand, earthing/PE conductor, installation method and applicable EIT / owner requirements separately before construction.
Length is one-way route length. For 1Φ and DC 2-wire, the formula already includes the return conductor factor (2).
DC assumptions | Value | Unit / method | Note
Copper temperature coefficient, αCu | 0.00393 | 1/°C | Used to adjust Rdc from 20°C to selected operating temperature.
DC default operating conductor temperature | 90 | °C | Editable in DC Calculator; datasheets allow 120°C for limited duration, but 90°C is the default design point.
DC default Voltage Drop target | 1.5% | % | Editable in DC Calculator; common reference target for PV string cable.
DC design minimum cell temperature | 10 | °C | Editable design assumption used for cold Voc check; confirm project climate and inverter design basis.
Default inverter maximum DC input voltage | 1500 | V DC | Editable design assumption; replace with the selected inverter datasheet value.
DC source / method | Reference | How used | Important limitation
PV module datasheet | 3.2.panel_datasheet_JKM700-725N-66HL5-BDV-Z2C2-OC.pdf | Uses the 725 Wp STC row: Vmp 41.00 V, Imp 17.69 A, Voc 49.20 V, Isc 18.74 A and temperature coefficients. | Confirm the final procurement module and any bifacial design gain separately.
Phelps Dodge PV cable | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf | Uses Rdc at 20°C, current-carrying capacities and manufacturer datasheet voltage-drop column where provided. | Verify exact cable construction, installation arrangement, derating and current-carrying method.
Bangkok Cable PV cable | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf | Uses Rdc at 20°C and current-carrying capacities from the attached table; operating-temperature VD is formula-calculated. | The attached table does not provide a separate voltage-drop column; confirm final catalogue values if required.
DC voltage-drop method | 2-wire DC; Rθ = R20 × [1 + α × (T−20)] | ΔV = 2 × I × L × Rθ / 1000; Power loss = I² × loop resistance; L is one-way. | Voltage Drop does not replace ampacity/derating, protection, connector, short-circuit or inverter checks.

## Cable Database
Cable Database ¦ Low-voltage CV in project list
Cable ID | Project description | No. cores | Area (sq.mm.) | Rdc @20°C (Ω/km) | α (1/°C) | R @ selected temp (Ω/km) | X default (Ω/km) | Cable status | Source
CV-FD 4C 10 | FD-0.6/1KV-CV 4C | 4 | 10 | 1.83 | 0.00393 | 2.3334 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 16 | FD-0.6/1KV-CV 1C | 1 | 16 | 1.15 | 0.00393 | 1.4664 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 4C 16 | FD-0.6/1KV-CV 4C | 4 | 16 | 1.15 | 0.00393 | 1.4664 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 25 | FD-0.6/1KV-CV 1C | 1 | 25 | 0.727 | 0.00393 | 0.927 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 4C 25 | FD-0.6/1KV-CV 4C | 4 | 25 | 0.727 | 0.00393 | 0.927 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 35 | FD-0.6/1KV-CV 1C | 1 | 35 | 0.524 | 0.00393 | 0.66815 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 4C 35 | FD-0.6/1KV-CV 4C | 4 | 35 | 0.524 | 0.00393 | 0.66815 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 50 | FD-0.6/1KV-CV 1C | 1 | 50 | 0.387 | 0.00393 | 0.49346 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 70 | FD-0.6/1KV-CV 1C | 1 | 70 | 0.268 | 0.00393 | 0.34173 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 4C 70 | FD-0.6/1KV-CV 4C | 4 | 70 | 0.268 | 0.00393 | 0.34173 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 95 | FD-0.6/1KV-CV 1C | 1 | 95 | 0.193 | 0.00393 | 0.24609 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 120 | FD-0.6/1KV-CV 1C | 1 | 120 | 0.153 | 0.00393 | 0.19509 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 150 | FD-0.6/1KV-CV 1C | 1 | 150 | 0.124 | 0.00393 | 0.15811 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 185 | FD-0.6/1KV-CV 1C | 1 | 185 | 0.0991 | 0.00393 | 0.12636 | 0.08 | Included in source file | Project list + IEC 60228 Rdc
CV-FD 1C 240 | FD-0.6/1KV-CV 1C | 1 | 240 | 0.0754 | 0.00393 | 0.096143 | 0.08 | Included in source file | Project list + IEC 60228 Rdc

## Panel Datasheet
PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp | PV Module Datasheet ¦ Jinko JKM700-725N-66HL5-BDV-Z2C2-OC ¦ Selected 725 Wp
Selected module characteristics (STC) | Value |  | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC | Electrical performance table from datasheet ¦ STC
Model | JKM700-725N-66HL5-BDV-Z2C2-OC |  | Pmax (Wp) | Vmp (V) | Imp (A) | Voc (V) | Isc (A) | Efficiency | Selection
Selected Pmax (Wp) | 725 |  | 700 | 40.42 | 17.32 | 48.4 | 18.4 | 22.54%
Vmp at STC (V) | 41 |  | 705 | 40.53 | 17.4 | 48.56 | 18.46 | 22.7%
Imp at STC (A) | 17.69 |  | 710 | 40.65 | 17.47 | 48.73 | 18.53 | 22.86%
Voc at STC (V) | 49.2 |  | 715 | 40.77 | 17.54 | 48.88 | 18.6 | 23.02%
Isc at STC (A) | 18.74 |  | 720 | 40.89 | 17.61 | 49.04 | 18.67 | 23.18%
Module efficiency | 23.35% |  | 725 | 41 | 17.69 | 49.2 | 18.74 | 23.35% | SELECTED
Maximum system voltage (V DC) | 1500
Maximum series fuse rating (A) | 35 |  | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc. | Design note: calculator uses STC electrical values for Voltage Drop and a separate minimum-cell-temperature check for Voc.
Temperature coefficient Pmax | -0.29%
Temperature coefficient Voc | -0.25% |  | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%. | STC: irradiance 1000 W/m², cell temperature 25 °C, AM 1.5. Datasheet notes power measurement tolerance ±3%.
Temperature coefficient Isc | 0.045%
Operating temperature | -40 °C to +70 °C
Cell technology | N-type mono-crystalline, bifacial, dual glass
Dimensions | 2384 × 1303 × 33 mm
Weight | 37.5 kg
Output cables | 4.0 mm²; (+) 400 mm, (-) 200 mm or customized
Connector | PV-JK03M/xy, PV-03M2/xy; PV-KST4-EVO2A/xy, PV-KBT4-EVO2A/xy
Source file | 3.2.panel_datasheet_JKM700-725N-66HL5-BDV-Z2C2-OC.pdf

## DC Cable Database
DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable | DC Cable Database ¦ H1Z2Z2-K PV Cable ¦ Phelps Dodge and Bangkok Cable
Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu. | Resistance values are datasheet maximum DC resistance at 20 °C. Rdc @ operating temp and loop mV/A/m are formula-driven using the selected operating temperature and αCu.
Cable ID | Manufacturer | Cable type | Area (mm²) | Rdc @20°C (Ω/km) | Datasheet VD (mV/A/m) | Ampacity free air (A) | Ampacity surface (A) | Ampacity two loaded / surface (A) | Rated voltage DC (kV) | Max conductor temp (°C) | Standard length (m) | Rdc @ operating temp (Ω/km) | Loop VD @ operating temp (mV/A/m) | Source / note
Phelps Dodge H1Z2Z2-K 2.5 mm² | Phelps Dodge | H1Z2Z2-K | 2.5 | 8.21 | 20.94 | 41 | 39 | 33 | 1.5 | 120 | 200 | 10.4686 | 20.9371 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 4 mm² | Phelps Dodge | H1Z2Z2-K | 4 | 5.09 | 12.98 | 55 | 52 | 44 | 1.5 | 120 | 200 | 6.4903 | 12.9805 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 6 mm² | Phelps Dodge | H1Z2Z2-K | 6 | 3.39 | 8.65 | 70 | 67 | 57 | 1.5 | 120 | 100 | 4.3226 | 8.6452 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 10 mm² | Phelps Dodge | H1Z2Z2-K | 10 | 1.95 | 4.97 | 98 | 93 | 79 | 1.5 | 120 | 100 | 2.4864 | 4.9729 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 16 mm² | Phelps Dodge | H1Z2Z2-K | 16 | 1.24 | 3.16 | 132 | 125 | 107 | 1.5 | 120 | 100 | 1.5811 | 3.1622 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 25 mm² | Phelps Dodge | H1Z2Z2-K | 25 | 0.795 | 2.03 | 176 | 167 | 142 | 1.5 | 120 | 100 | 1.0137 | 2.0274 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 35 mm² | Phelps Dodge | H1Z2Z2-K | 35 | 0.565 | 1.44 | 218 | 207 | 176 | 1.5 | 120 | 100 | 0.72043 | 1.4409 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 50 mm² | Phelps Dodge | H1Z2Z2-K | 50 | 0.393 | 1 | 276 | 262 | 221 | 1.5 | 120 | 100 | 0.50111 | 1.0022 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 70 mm² | Phelps Dodge | H1Z2Z2-K | 70 | 0.277 | 0.71 | 347 | 330 | 278 | 1.5 | 120 | 500 | 0.3532 | 0.70641 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 95 mm² | Phelps Dodge | H1Z2Z2-K | 95 | 0.21 | 0.54 | 416 | 395 | 333 | 1.5 | 120 | 500 | 0.26777 | 0.53554 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 120 mm² | Phelps Dodge | H1Z2Z2-K | 120 | 0.164 | 0.42 | 488 | 464 | 390 | 1.5 | 120 | 500 | 0.20912 | 0.41823 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 150 mm² | Phelps Dodge | H1Z2Z2-K | 150 | 0.132 | 0.34 | 566 | 538 | 453 | 1.5 | 120 | 500 | 0.16831 | 0.33663 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 185 mm² | Phelps Dodge | H1Z2Z2-K | 185 | 0.108 | 0.28 | 644 | 612 | 515 | 1.5 | 120 | 500 | 0.13771 | 0.27542 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 240 mm² | Phelps Dodge | H1Z2Z2-K | 240 | 0.0817 | 0.21 | 775 | 736 | 620 | 1.5 | 120 | 500 | 0.10418 | 0.20835 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Bangkok Cable H1Z2Z2-K 1.5 mm² | Bangkok Cable | H1Z2Z2-K | 1.5 | 13.7 |  | 30 | 29 | 24 | 1.5 | 120 | 200 | 17.4689 | 34.9377 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 2.5 mm² | Bangkok Cable | H1Z2Z2-K | 2.5 | 8.21 |  | 41 | 39 | 33 | 1.5 | 120 | 200 | 10.4686 | 20.9371 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 4 mm² | Bangkok Cable | H1Z2Z2-K | 4 | 5.09 |  | 55 | 52 | 44 | 1.5 | 120 | 200 | 6.4903 | 12.9805 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 6 mm² | Bangkok Cable | H1Z2Z2-K | 6 | 3.39 |  | 70 | 67 | 57 | 1.5 | 120 | 100 | 4.3226 | 8.6452 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 10 mm² | Bangkok Cable | H1Z2Z2-K | 10 | 1.95 |  | 98 | 93 | 79 | 1.5 | 120 | 100 | 2.4864 | 4.9729 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 16 mm² | Bangkok Cable | H1Z2Z2-K | 16 | 1.24 |  | 132 | 125 | 107 | 1.5 | 120 | 100 | 1.5811 | 3.1622 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 25 mm² | Bangkok Cable | H1Z2Z2-K | 25 | 0.795 |  | 176 | 167 | 142 | 1.5 | 120 | 100 | 1.0137 | 2.0274 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 35 mm² | Bangkok Cable | H1Z2Z2-K | 35 | 0.565 |  | 218 | 207 | 176 | 1.5 | 120 | 100 | 0.72043 | 1.4409 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 50 mm² | Bangkok Cable | H1Z2Z2-K | 50 | 0.393 |  | 276 | 262 | 221 | 1.5 | 120 | 100 | 0.50111 | 1.0022 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 70 mm² | Bangkok Cable | H1Z2Z2-K | 70 | 0.277 |  | 347 | 330 | 278 | 1.5 | 120 | 500 | 0.3532 | 0.70641 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 95 mm² | Bangkok Cable | H1Z2Z2-K | 95 | 0.21 |  | 416 | 395 | 333 | 1.5 | 120 | 500 | 0.26777 | 0.53554 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 120 mm² | Bangkok Cable | H1Z2Z2-K | 120 | 0.164 |  | 488 | 464 | 390 | 1.5 | 120 | 500 | 0.20912 | 0.41823 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 150 mm² | Bangkok Cable | H1Z2Z2-K | 150 | 0.132 |  | 566 | 538 | 453 | 1.5 | 120 | 500 | 0.16831 | 0.33663 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 185 mm² | Bangkok Cable | H1Z2Z2-K | 185 | 0.108 |  | 644 | 612 | 515 | 1.5 | 120 | 500 | 0.13771 | 0.27542 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 240 mm² | Bangkok Cable | H1Z2Z2-K | 240 | 0.0817 |  | 775 | 736 | 620 | 1.5 | 120 | 500 | 0.10418 | 0.20835 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table

## Calculator
CV Low-Voltage Voltage-Drop Calculator ¦ Design limit ≤ 3%
1) Enter or select yellow cells. Results update automatically. All lengths are one-way route lengths.
INPUT | VALUE | 2) Calculated result
Cable ID | CV-FD 1C 70 | Rdc @20°C (Ω/km) | 0.268
System | 3Φ AC | R at operating temp (Ω/km) | 0.34173
Nominal voltage (V) | 400 | sin φ | 0.52678
Load current (A) | 100 | Circuit multiplier | 1.7321
Power factor (AC only) | 0.85 | Effective impedance term (Ω/km) | 0.33261
One-way route length (m) | 100 | Voltage drop ΔV (V) | 5.761
Voltage-drop limit | 3% | Voltage drop | 1.44%
Conductor temperature (°C) | 90 | Result | PASS ≤ limit
Reactance X (Ω/km) | 0.08 | Maximum route length (m) | 208.2979
Notes / circuit name | Example: LV feeder | Margin to limit (m) | 108.2979
|  | Formula used | √3×I×L×(Rcosφ+Xsinφ)
Important: This is a voltage-drop check, not a cable ampacity selection. Verify ampacity/derating, fault duty, protection and EIT/project requirements separately.

## Quick Reference
Quick Reference ¦ Maximum one-way route length for voltage drop ≤ limit
Common inputs | Value |  | Preset scenarios (change current / PF / voltage in the header cells as needed)
Voltage-drop limit | 3%
Conductor temperature (°C) | 90
Cable ID | Cores | Area (sq.mm.) | R at temp (Ω/km) | X (Ω/km) | 3Φ 400V PF 0.80 @100A | 3Φ 400V PF 0.95 @100A | 3Φ 400V PF 1.00 @100A | 1Φ 230V PF 0.95 @32A | DC 1000V @100A | m per A: 3Φ 400V PF1
CV-FD 4C 10 | 4 | 10 | 2.3334 | 0.08 | 36.1834 | 30.9055 | 29.691 | 48.0932 | 64.283 | 2969.1031
CV-FD 1C 16 | 1 | 16 | 1.4664 | 0.08 | 56.7378 | 48.8581 | 47.2475 | 76.0299 | 102.2938 | 4724.7467
CV-FD 4C 16 | 4 | 16 | 1.4664 | 0.08 | 56.7378 | 48.8581 | 47.2475 | 76.0299 | 102.2938 | 4724.7467
CV-FD 1C 25 | 1 | 25 | 0.927 | 0.08 | 87.7434 | 76.5017 | 74.7381 | 119.0473 | 161.8127 | 7473.8084
CV-FD 4C 25 | 4 | 25 | 0.927 | 0.08 | 87.7434 | 76.5017 | 74.7381 | 119.0473 | 161.8127 | 7473.8084
CV-FD 1C 35 | 1 | 35 | 0.66815 | 0.08 | 118.9346 | 105.0166 | 103.692 | 163.4204 | 224.4997 | 10369.1961
CV-FD 4C 35 | 4 | 35 | 0.66815 | 0.08 | 118.9346 | 105.0166 | 103.692 | 163.4204 | 224.4997 | 10369.1961
CV-FD 1C 50 | 1 | 50 | 0.49346 | 0.08 | 156.4737 | 140.3122 | 140.3995 | 218.3454 | 303.9737 | 14039.945
CV-FD 1C 70 | 1 | 70 | 0.34173 | 0.08 | 215.5757 | 198.1636 | 202.741 | 308.3701 | 438.9471 | 20274.0997
CV-FD 4C 70 | 4 | 70 | 0.34173 | 0.08 | 215.5757 | 198.1636 | 202.741 | 308.3701 | 438.9471 | 20274.0997
CV-FD 1C 95 | 1 | 95 | 0.24609 | 0.08 | 282.9276 | 267.7364 | 281.5264 | 416.6351 | 609.5224 | 28152.6359
CV-FD 1C 120 | 1 | 120 | 0.19509 | 0.08 | 339.4976 | 329.4191 | 355.128 | 512.622 | 768.8747 | 35512.8022
CV-FD 1C 150 | 1 | 150 | 0.15811 | 0.08 | 397.0546 | 395.4752 | 438.1822 | 615.4146 | 948.6922 | 43818.2156
CV-FD 1C 185 | 1 | 185 | 0.12636 | 0.08 | 464.6996 | 477.7271 | 548.2804 | 743.41 | 1187.0619 | 54828.0397
CV-FD 1C 240 | 1 | 240 | 0.096143 | 0.08 | 554.6377 | 595.6394 | 720.6179 | 926.8979 | 1560.1835 | 72061.7869
Tip: maximum length is inversely proportional to load current. Use the Calculator sheet for the exact project load, voltage, PF and route length.

## Project Cable List
Project Cable List ¦ Extracted Low Voltage CV items
Cable ID used in tool | Original-style source description | Classification | Included?
CV-FD 4C 10 | AC Cable (FD-0.6/1KV-CV 4C) 4C 10 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 16 | AC Cable (FD-0.6/1KV-CV 1C) 1C 16 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 4C 16 | AC Cable (FD-0.6/1KV-CV 4C) 4C 16 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 25 | AC Cable (FD-0.6/1KV-CV 1C) 1C 25 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 4C 25 | AC Cable (FD-0.6/1KV-CV 4C) 4C 25 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 35 | AC Cable (FD-0.6/1KV-CV 1C) 1C 35 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 4C 35 | AC Cable (FD-0.6/1KV-CV 4C) 4C 35 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 50 | AC Cable (FD-0.6/1KV-CV 1C) 1C 50 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 70 | AC Cable (FD-0.6/1KV-CV 1C) 1C 70 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 4C 70 | AC Cable (FD-0.6/1KV-CV 4C) 4C 70 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 95 | AC Cable (FD-0.6/1KV-CV 1C) 1C 95 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 120 | AC Cable (FD-0.6/1KV-CV 1C) 1C 120 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 150 | AC Cable (FD-0.6/1KV-CV 1C) 1C 150 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 185 | AC Cable (FD-0.6/1KV-CV 1C) 1C 185 sq.mm. | Low voltage 0.6/1 kV CV | Yes
CV-FD 1C 240 | AC Cable (FD-0.6/1KV-CV 1C) 1C 240 sq.mm. | Low voltage 0.6/1 kV CV | Yes

## DC Calculator
DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable | DC PV String Voltage-Drop Calculator ¦ Jinko 725 Wp ¦ Phelps Dodge / Bangkok Cable
Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors. | Enter or select yellow cells. All lengths are one-way route lengths. The DC formula includes the positive and negative conductors.
INPUT | VALUE |  | CALCULATED RESULT | VALUE
Cable ID | Bangkok Cable H1Z2Z2-K 6 mm² |  | Rdc @20°C (Ω/km) | 3.39
Modules in series (modules/string) | 15 |  | Vmp/module (V) | 41
One-way route length (m) | 75 |  | Imp/module (A) | 17.69
Voltage-drop limit | 1.5% |  | Voc/module STC (V) | 49.2
Operating conductor temperature (°C) | 90 |  | String Vmp (V) | 615
Design minimum cell temperature (°C) | 10 |  | String Imp (A) | 17.69
Inverter maximum DC input voltage (V) | 1100 |  | String Pmp at Vmp×Imp (W) | 10879.35
Notes / circuit name | Example: 15-module string to inverter |  | Voc/module at min cell temp (V) | 51.045
Cable selection basis | Voltage Drop + ampacity check only |  | String Voc at min cell temp (V) | 765.675
|  |  | Rdc @ operating temp (Ω/km) | 4.3226
|  |  | Loop resistance (Ω) | 0.64839
|  |  | Voltage drop ΔV (V) | 11.47
|  |  | Voltage drop (%) | 1.865%
|  |  | Power loss (W) | 202.9041
|  |  | Power loss (%) | 1.865%
|  |  | Maximum one-way route length (m) | 60.3205
|  |  | Margin to limit (m) | -14.6795
|  |  | Ampacity: two loaded / surface (A) | 57
|  |  | Ampacity status | PASS
|  |  | Cable rated voltage (V DC) | 1500
|  |  | Voltage rating status | PASS
|  |  | Cable max conductor temp (°C) | 120
|  |  | Temperature input status | PASS
|  |  | Overall result | CHECK
|  |  | Formula: ΔV = 2 × I × L × Rθ / 1000, where Rθ is in Ω/km and L is one-way in m. Power loss = I² × loop resistance. | Formula: ΔV = 2 × I × L × Rθ / 1000, where Rθ is in Ω/km and L is one-way in m. Power loss = I² × loop resistance. | Formula: ΔV = 2 × I × L × Rθ / 1000, where Rθ is in Ω/km and L is one-way in m. Power loss = I² × loop resistance. | Formula: ΔV = 2 × I × L × Rθ / 1000, where Rθ is in Ω/km and L is one-way in m. Power loss = I² × loop resistance. | Formula: ΔV = 2 × I × L × Rθ / 1000, where Rθ is in Ω/km and L is one-way in m. Power loss = I² × loop resistance.
Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately. | Important: this is a Voltage Drop and preliminary ampacity check. Verify installation method, grouping/temperature derating, connectors, protection, short-circuit duty, earthing and inverter limits separately.

## DC Quick Reference
DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target | DC Quick Reference ¦ Maximum one-way route length for Voltage Drop target
Common inputs | Value |  | Reference settings | Value
Selected Pmax (Wp) | 725 |  | Operating conductor temperature (°C) | 90
Vmp/module (V) | 41 |  | Minimum cell temperature (°C) | 10
Imp/module (A) | 17.69 |  | Length basis | One-way route length
Voltage-drop target | 1.5% |  | Cable sizes highlighted | 4 / 6 / 10 mm²
|  |  | Method | 2-wire DC; positive + negative
Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings | Common sizes ¦ Maximum one-way length at 10-module, 15-module and 20-module strings
Cable ID | Manufacturer | Area (mm²) | Rdc @90°C (Ω/km) | Ampacity two loaded / surface (A) | 0.5% | 1% | 1.5% | 2% | 15 modules @1.5% (m) | 20 modules @1.5% (m)
Phelps Dodge H1Z2Z2-K 4 mm² | Phelps Dodge | 4 | 6.4903 | 44 | 8.9276 | 17.8552 | 26.7828 | 35.7103 | 40.1741 | 53.5655
Phelps Dodge H1Z2Z2-K 6 mm² | Phelps Dodge | 6 | 4.3226 | 57 | 13.4045 | 26.8091 | 40.2136 | 53.6182 | 60.3205 | 80.4273
Phelps Dodge H1Z2Z2-K 10 mm² | Phelps Dodge | 10 | 2.4864 | 79 | 23.3033 | 46.6066 | 69.9099 | 93.2131 | 104.8648 | 139.8197
Bangkok Cable H1Z2Z2-K 4 mm² | Bangkok Cable | 4 | 6.4903 | 44 | 8.9276 | 17.8552 | 26.7828 | 35.7103 | 40.1741 | 53.5655
Bangkok Cable H1Z2Z2-K 6 mm² | Bangkok Cable | 6 | 4.3226 | 57 | 13.4045 | 26.8091 | 40.2136 | 53.6182 | 60.3205 | 80.4273
Bangkok Cable H1Z2Z2-K 10 mm² | Bangkok Cable | 10 | 2.4864 | 79 | 23.3033 | 46.6066 | 69.9099 | 93.2131 | 104.8648 | 139.8197
All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes | All cable sizes in source datasheets ¦ Target = 1.5% ¦ Use this table to compare manufacturers and larger sizes
Cable ID | Manufacturer | Area (mm²) | Rdc @20°C | Rdc @90°C | Ampacity two loaded / surface | 10 modules Lmax (m) | 15 modules Lmax (m) | 20 modules Lmax (m) | Standard length (m) | Source
Phelps Dodge H1Z2Z2-K 2.5 mm² | Phelps Dodge | 2.5 | 8.21 | 10.4686 | 33 | 16.6047 | 24.907 | 33.2093 | 200 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 4 mm² | Phelps Dodge | 4 | 5.09 | 6.4903 | 44 | 26.7828 | 40.1741 | 53.5655 | 200 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 6 mm² | Phelps Dodge | 6 | 3.39 | 4.3226 | 57 | 40.2136 | 60.3205 | 80.4273 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 10 mm² | Phelps Dodge | 10 | 1.95 | 2.4864 | 79 | 69.9099 | 104.8648 | 139.8197 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 16 mm² | Phelps Dodge | 16 | 1.24 | 1.5811 | 107 | 109.9389 | 164.9083 | 219.8778 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 25 mm² | Phelps Dodge | 25 | 0.795 | 1.0137 | 142 | 171.477 | 257.2155 | 342.954 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 35 mm² | Phelps Dodge | 35 | 0.565 | 0.72043 | 176 | 241.2818 | 361.9227 | 482.5636 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 50 mm² | Phelps Dodge | 50 | 0.393 | 0.50111 | 221 | 346.881 | 520.3215 | 693.762 | 100 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 70 mm² | Phelps Dodge | 70 | 0.277 | 0.3532 | 278 | 492.1452 | 738.2178 | 984.2904 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 95 mm² | Phelps Dodge | 95 | 0.21 | 0.26777 | 333 | 649.163 | 973.7445 | 1298.326 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 120 mm² | Phelps Dodge | 120 | 0.164 | 0.20912 | 390 | 831.2453 | 1246.8679 | 1662.4906 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 150 mm² | Phelps Dodge | 150 | 0.132 | 0.16831 | 453 | 1032.7593 | 1549.1389 | 2065.5186 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 185 mm² | Phelps Dodge | 185 | 0.108 | 0.13771 | 515 | 1262.2614 | 1893.392 | 2524.5227 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Phelps Dodge H1Z2Z2-K 240 mm² | Phelps Dodge | 240 | 0.0817 | 0.10418 | 620 | 1668.5952 | 2502.8928 | 3337.1904 | 500 | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; datasheet VD column
Bangkok Cable H1Z2Z2-K 1.5 mm² | Bangkok Cable | 1.5 | 13.7 | 17.4689 | 24 | 9.9507 | 14.926 | 19.9013 | 200 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 2.5 mm² | Bangkok Cable | 2.5 | 8.21 | 10.4686 | 33 | 16.6047 | 24.907 | 33.2093 | 200 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 4 mm² | Bangkok Cable | 4 | 5.09 | 6.4903 | 44 | 26.7828 | 40.1741 | 53.5655 | 200 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 6 mm² | Bangkok Cable | 6 | 3.39 | 4.3226 | 57 | 40.2136 | 60.3205 | 80.4273 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 10 mm² | Bangkok Cable | 10 | 1.95 | 2.4864 | 79 | 69.9099 | 104.8648 | 139.8197 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 16 mm² | Bangkok Cable | 16 | 1.24 | 1.5811 | 107 | 109.9389 | 164.9083 | 219.8778 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 25 mm² | Bangkok Cable | 25 | 0.795 | 1.0137 | 142 | 171.477 | 257.2155 | 342.954 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 35 mm² | Bangkok Cable | 35 | 0.565 | 0.72043 | 176 | 241.2818 | 361.9227 | 482.5636 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 50 mm² | Bangkok Cable | 50 | 0.393 | 0.50111 | 221 | 346.881 | 520.3215 | 693.762 | 100 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 70 mm² | Bangkok Cable | 70 | 0.277 | 0.3532 | 278 | 492.1452 | 738.2178 | 984.2904 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 95 mm² | Bangkok Cable | 95 | 0.21 | 0.26777 | 333 | 649.163 | 973.7445 | 1298.326 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 120 mm² | Bangkok Cable | 120 | 0.164 | 0.20912 | 390 | 831.2453 | 1246.8679 | 1662.4906 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 150 mm² | Bangkok Cable | 150 | 0.132 | 0.16831 | 453 | 1032.7593 | 1549.1389 | 2065.5186 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 185 mm² | Bangkok Cable | 185 | 0.108 | 0.13771 | 515 | 1262.2614 | 1893.392 | 2524.5227 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table
Bangkok Cable H1Z2Z2-K 240 mm² | Bangkok Cable | 240 | 0.0817 | 0.10418 | 620 | 1668.5952 | 2502.8928 | 3337.1904 | 500 | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; attached table

## DC Summary
DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length | DC Design Summary ¦ Jinko 725 Wp ¦ Voltage Drop target 1.5% ¦ One-way route length
Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets. | Common selection summary for 4, 6 and 10 mm² H1Z2Z2-K PV cable. Values are formula-driven from the Panel Datasheet and DC Cable Database sheets.
Modules/string | String Vmp (V) | String Pmp (W) | Manufacturer | Cable size (mm²) | Lmax @1.5% (m) | ΔV @50m (V) | ΔV @50m (%) | Power loss @50m (W) | Ampacity status | Quick use | Cable ID
10 | 410 | 7252.9 | Phelps Dodge | 4 | 26.7828 | 11.4813 | 2.8% | 203.1036 | PASS | Consider larger cable | Phelps Dodge H1Z2Z2-K 4 mm²
10 | 410 | 7252.9 | Phelps Dodge | 6 | 40.2136 | 7.6467 | 1.865% | 135.2694 | PASS | Consider larger cable | Phelps Dodge H1Z2Z2-K 6 mm²
10 | 410 | 7252.9 | Phelps Dodge | 10 | 69.9099 | 4.3985 | 1.073% | 77.8098 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 10 mm²
10 | 410 | 7252.9 | Bangkok Cable | 4 | 26.7828 | 11.4813 | 2.8% | 203.1036 | PASS | Consider larger cable | Bangkok Cable H1Z2Z2-K 4 mm²
10 | 410 | 7252.9 | Bangkok Cable | 6 | 40.2136 | 7.6467 | 1.865% | 135.2694 | PASS | Consider larger cable | Bangkok Cable H1Z2Z2-K 6 mm²
10 | 410 | 7252.9 | Bangkok Cable | 10 | 69.9099 | 4.3985 | 1.073% | 77.8098 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 10 mm²
15 | 615 | 10879.35 | Phelps Dodge | 4 | 40.1741 | 11.4813 | 1.867% | 203.1036 | PASS | Consider larger cable | Phelps Dodge H1Z2Z2-K 4 mm²
15 | 615 | 10879.35 | Phelps Dodge | 6 | 60.3205 | 7.6467 | 1.243% | 135.2694 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 6 mm²
15 | 615 | 10879.35 | Phelps Dodge | 10 | 104.8648 | 4.3985 | 0.7152% | 77.8098 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 10 mm²
15 | 615 | 10879.35 | Bangkok Cable | 4 | 40.1741 | 11.4813 | 1.867% | 203.1036 | PASS | Consider larger cable | Bangkok Cable H1Z2Z2-K 4 mm²
15 | 615 | 10879.35 | Bangkok Cable | 6 | 60.3205 | 7.6467 | 1.243% | 135.2694 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 6 mm²
15 | 615 | 10879.35 | Bangkok Cable | 10 | 104.8648 | 4.3985 | 0.7152% | 77.8098 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 10 mm²
20 | 820 | 14505.8 | Phelps Dodge | 4 | 53.5655 | 11.4813 | 1.4% | 203.1036 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 4 mm²
20 | 820 | 14505.8 | Phelps Dodge | 6 | 80.4273 | 7.6467 | 0.9325% | 135.2694 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 6 mm²
20 | 820 | 14505.8 | Phelps Dodge | 10 | 139.8197 | 4.3985 | 0.5364% | 77.8098 | PASS | OK at 50m | Phelps Dodge H1Z2Z2-K 10 mm²
20 | 820 | 14505.8 | Bangkok Cable | 4 | 53.5655 | 11.4813 | 1.4% | 203.1036 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 4 mm²
20 | 820 | 14505.8 | Bangkok Cable | 6 | 80.4273 | 7.6467 | 0.9325% | 135.2694 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 6 mm²
20 | 820 | 14505.8 | Bangkok Cable | 10 | 139.8197 | 4.3985 | 0.5364% | 77.8098 | PASS | OK at 50m | Bangkok Cable H1Z2Z2-K 10 mm²
Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check. | Interpretation: select a cable with Lmax greater than the measured route length and then verify ampacity after actual installation derating. Lmax is voltage-drop-only and does not replace a complete cable design check.