## Input
PV-DC Cable Tray Sizing Calculator
แก้ไขเฉพาะช่องสีเหลือง: ค่า OD ต้องใช้จาก Datasheet ผู้ผลิตสายจริง ผลลัพธ์เป็นความจุทางกายภาพของราง ไม่ใช่การยืนยัน Ampacity
Cable Size (mm²) | Cable OD (mm) | Cable Area (mm²) | หมายเหตุ | Design Parameter | Value
4 | 6 | 28.2743 | ค่าเริ่มต้นสมมติ — แก้ตาม Datasheet | Maximum tray fill | 20%
6 | 7 | 38.4845 | ค่าเริ่มต้นสมมติ — แก้ตาม Datasheet | Usable tray width | 80%
10 | 8 | 50.2655 | ค่าเริ่มต้นสมมติ — แก้ตาม Datasheet | Conductors per string | 2
|  |  |  | Reserve / expansion | 0%
หลักการคำนวณ
1 | Area limit | พื้นที่สายรวม ≤ พื้นที่ภายในราง × Maximum tray fill
2 | Width limit | ผลรวม OD ของสายชั้นเดียว ≤ ความกว้างราง × Usable tray width
3 | Maximum conductors | ใช้ค่าต่ำสุดระหว่าง Area limit และ Width limit และปัดลงเป็นเลขคู่
4 | Maximum strings | Maximum conductors ÷ 2 (PV+ และ PV− ต่อ 1 String)
5 | Engineering check | ต้องตรวจ Grouping, Ambient/Rooftop temperature, Tray cover และ Ampacity แยกต่างหาก
6 | Tray dimensions | ใช้ขนาดภายในจริง หากผู้ผลิตระบุ Internal Dimension ต่างจาก Nominal Size

## Cable Tray Selection
ตารางเลือก Cable Tray สำหรับสาย PV-DC 4, 6 และ 10 mm²
[7 empty] | 20% Fill | 0.8W | Select min.
No. | Tray Type | Width (mm) | Height (mm) | Tray Area (mm²) | Allowable Area (mm²) | 4 mm² OD | 4 mm² Area Limit | 4 mm² Width Limit | 4 mm² Max Cables | 4 mm² Max Strings | 6 mm² OD | 6 mm² Area Limit | 6 mm² Width Limit | 6 mm² Max Cables | 6 mm² Max Strings | 10 mm² OD | 10 mm² Area Limit | 10 mm² Width Limit | 10 mm² Max Cables | 10 mm² Max Strings | Recommended Selection Check | Remark
1 | Cable Tray with cover | 50 | 50 | 2500 | 500 | 6 | 17 | 6 | 6 | 3 | 7 | 12 | 5 | 4 | 2 | 8 | 9 | 5 | 4 | 2 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
2 | Basket Tray with cover | 50 | 50 | 2500 | 500 | 6 | 17 | 6 | 6 | 3 | 7 | 12 | 5 | 4 | 2 | 8 | 9 | 5 | 4 | 2 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
3 | Cable Tray with cover | 100 | 100 | 10000 | 2000 | 6 | 70 | 13 | 12 | 6 | 7 | 51 | 11 | 10 | 5 | 8 | 39 | 10 | 10 | 5 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
4 | Basket Tray with cover | 150 | 50 | 7500 | 1500 | 6 | 53 | 20 | 20 | 10 | 7 | 38 | 17 | 16 | 8 | 8 | 29 | 15 | 14 | 7 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
5 | Cable Tray with cover | 200 | 100 | 20000 | 4000 | 6 | 141 | 26 | 26 | 13 | 7 | 103 | 22 | 22 | 11 | 8 | 79 | 20 | 20 | 10 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
6 | Cable Tray with cover | 300 | 100 | 30000 | 6000 | 6 | 212 | 40 | 40 | 20 | 7 | 155 | 34 | 34 | 17 | 8 | 119 | 30 | 30 | 15 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
7 | Basket Tray with cover | 400 | 50 | 20000 | 4000 | 6 | 141 | 53 | 52 | 26 | 7 | 103 | 45 | 44 | 22 | 8 | 79 | 40 | 40 | 20 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
8 | Cable Tray with cover | 400 | 100 | 40000 | 8000 | 6 | 282 | 53 | 52 | 26 | 7 | 207 | 45 | 44 | 22 | 8 | 159 | 40 | 40 | 20 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
9 | Cable Tray with cover | 500 | 100 | 50000 | 10000 | 6 | 353 | 66 | 66 | 33 | 7 | 259 | 57 | 56 | 28 | 8 | 198 | 50 | 50 | 25 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
10 | Cable Tray with cover | 600 | 100 | 60000 | 12000 | 6 | 424 | 80 | 80 | 40 | 7 | 311 | 68 | 68 | 34 | 8 | 238 | 60 | 60 | 30 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
11 | Cable Tray with cover | 700 | 100 | 70000 | 14000 | 6 | 495 | 93 | 92 | 46 | 7 | 363 | 80 | 80 | 40 | 8 | 278 | 70 | 70 | 35 | Usable — verify derating | Max cables = physical tray capacity; verify ampacity separately
INT = ไม่เอาเศษ

## Quick Selection
Quick Selection — จำนวนสายสูงสุดที่แนะนำจากสูตร
Tray Type | Size (mm) | 4 mm² Max Cables | 4 mm² Strings | 6 mm² Max Cables | 6 mm² Strings | 10 mm² Max Cables | 10 mm² Strings
Cable Tray with cover | 50x50 | 6 | 3 | 4 | 2 | 4 | 2
Basket Tray with cover | 50x50 | 6 | 3 | 4 | 2 | 4 | 2
Cable Tray with cover | 100x100 | 12 | 6 | 10 | 5 | 10 | 5
Basket Tray with cover | 150x50 | 20 | 10 | 16 | 8 | 14 | 7
Cable Tray with cover | 200x100 | 26 | 13 | 22 | 11 | 20 | 10
Cable Tray with cover | 300x100 | 40 | 20 | 34 | 17 | 30 | 15
Basket Tray with cover | 400x50 | 52 | 26 | 44 | 22 | 40 | 20
Cable Tray with cover | 400x100 | 52 | 26 | 44 | 22 | 40 | 20
Cable Tray with cover | 500x100 | 66 | 33 | 56 | 28 | 50 | 25
Cable Tray with cover | 600x100 | 80 | 40 | 68 | 34 | 60 | 30
Cable Tray with cover | 700x100 | 92 | 46 | 80 | 40 | 70 | 35
หมายเหตุ
OD เริ่มต้น | 4 mm² = 6 mm | 6 mm² = 7 mm | 10 mm² = 8 mm
การใช้งาน | แก้ OD ใน Sheet Input แล้วตารางทั้งหมดจะคำนวณใหม่
ข้อจำกัด | ไม่รวมการตรวจพิกัดกระแสหลัง Derating และไม่ควรใช้แทน Cable Datasheet/Engineering Calculation