## Read Me
Cable Containment Data Register — Expert Update 2026-08-01 / Rev.4 | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs | Cable Containment Data Register - Example Inputs
Field | Value / instruction
Status | PRELIMINARY / EXAMPLE INPUTS - NOT APPROVED FOR CONSTRUCTION
Conduit selected | Panasonic White Conduit - IMC (ANSI/UL)
Cable ladder selected | KJL KLSG - Hot-Dip Galvanized Cable Ladder
Purpose | Formula-driven EIT physical-capacity screening for Panasonic IMC, cable ladder, cable tray and wireway. Rev.3 adds three input examples, Jinko 725 Wp reference, PV cable sizes 4/6/10/16 mm² and an editable Vendor Register OD master linked to all PV containment views.
Conduit warning | The catalogue gives nominal OD and minimum wall thickness, not a certified actual internal diameter. ID_screening is a formula for screening only.
Ladder warning | Nominal W x H is not automatically usable cable width/depth. Confirm shop drawing/profile and support arrangement before fill calculation.
Engineering hold point | Physical maximum is not an ampacity approval. Confirm actual IMC ID, usable ladder width, exact cable OD, circuit grouping, ambient factors, bending/pulling, support loads, earthing and corrosion class.
Rev.4 central link | Fill Calculator dropdowns use IMC Max Count!B10:B13; the OD returned from IMC Max Count!E10:E13 is linked to Vendor Register Phelps Dodge OD inputs.
IMC selection | IMC Max Count uses total Qty entered in the cable mix for 53% / 31% / 40% screening and provides single- or parallel-conduit recommendations.
Area-only calculators | Fill Calculator and Wireway Calculator use physical area fill only; no 0.8W condition is applied in either calculator.
Separate width screen | PV Wireway and PV Ladder/Cable Tray retain the requested additional ΣD_cable ≤ 0.8W screen where applicable.
Use restriction | Confirm exact cable OD, actual certified IMC internal diameter, ampacity, derating, support and bonding before IFC.

## EIT Rules
EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules | EIT / วสท. – Cable Containment Decision Rules
ID | ระบบ | หลักเกณฑ์ใช้งาน | ค่าหลัก | ผลต่อ PV 1C / FD-CV | แหล่งอ้างอิง | สถานะ
EIT-WW-01 | Wireway | ช่วงปกติ ห้ามพื้นที่หน้าตัดรวมของสายรวมฉนวนเกินพื้นที่ภายในราง | 20% | คำนวณจากพื้นที่หน้าตัดภายนอกจริงของสายทุกเส้น | วสท. 022001-22 ข้อ 5.12; Bangkok Cable Guide PDF p.383-384 | DESIGN RULE
EIT-WW-02 | Wireway | จุดต่อ/แยกที่เปิดตรวจได้ พื้นที่รวมสายและ connector | ไม่เกิน 75% | ใช้เฉพาะบริเวณจุดต่อ; ต้องรวม connector และตรวจการเข้าถึง | วสท. 022001-22 ข้อ 5.12 | DESIGN RULE
EIT-WW-03 | Wireway | เมื่อมีตัวนำกระแสเกิน 30 เส้น ต้องตรวจ ampacity/grouping เพิ่ม | >30 CCC = derating check | นับตัวนำที่มีกระแส ไม่ใช่นับจำนวน jacket; PE ไม่นับ และ neutral พิจารณาตามโหลด/ฮาร์มอนิก | Bangkok Cable Guide PDF p.383; วสท. 022001-22 | HOLD POINT
EIT-WW-04 | Wireway | ตัวนำวงจรเดียวกัน รวมถึง PE ต้องจัดกลุ่ม/เดินร่วมกัน | ทุกวงจร | PV +/− ต้องเดินคู่ชิดกัน; AC phase/neutral/PE ต้องจัดกลุ่ม | วสท. 022001-22 ข้อ 5.12 | DESIGN RULE
EIT-SEP-01 | AC/DC | แม้ฉนวนที่เหมาะสมอาจอนุญาตให้อยู่ใน enclosure เดียวกันได้ แนวทางโครงการให้แยก AC/DC | Separate หรือ solid divider | ลดความเสี่ยงสับสน, EMC, maintenance และเหตุฉุกเฉิน | Bangkok Cable Guide PDF p.352; project engineering rule | PROJECT RULE
EIT-TR-01 | Cable ladder/tray | Cable tray/ladder ไม่มีเกณฑ์ fill 20% แบบ wireway; ต้องใช้ชนิดสายและตารางความกว้าง/พื้นที่ตามข้อ 5.15 | No universal fill % | ห้ามใช้สูตร 20% ตัดสิน ladder | วสท. 022001-22 ข้อ 5.15 และตาราง 5-7 | DESIGN RULE
EIT-TR-02 | Cable ladder/tray | สายแกนเดียวมีเปลือก วางตรงบนรางได้เมื่อขนาดตัวนำไม่น้อยกว่า 25 mm²; สายหลายแกนวางได้ทุกขนาดตามเงื่อนไข | 1C ≥25 mm² | PV H1Z2Z2-K 4/6/10 mm² ไม่วางเปิดตรงบน ladder ภายใต้เกณฑ์ทั่วไป; FD-CV 1C ≥25 mm² จึงพิจารณาได้ | Bangkok Cable Guide PDF p.241; วสท. 022001-22 ข้อ 5.15 | CRITICAL
EIT-TR-03 | Cable ladder/tray | สายไม่มีเปลือก เช่น IEC 01/THW ห้ามวางตรงบน tray/ladder | Not permitted direct | ต้องอยู่ในท่อ/ช่องเดินสายที่เหมาะสม | Bangkok Cable Guide PDF p.240-241 | CRITICAL
EIT-TR-04 | Cable ladder/tray | จัดสายชั้นเดียวหรือ trefoil ตามชนิดวงจร ไม่ซ้อนหลายชั้น; มัดสาย 1C ของวงจรเดียวกันเป็นกลุ่ม | Single layer / trefoil | FD-CV 1C วงจร 3 เฟสต้องจัดกลุ่มและรักษาสมมาตร โดยเฉพาะวงจรขนาน | Bangkok Cable Guide PDF p.241; วสท. 022001-22 | DESIGN RULE
EIT-TR-05 | Cable ladder/tray | ช่องเปิดไม่น้อยกว่า 30% เป็นนิยามรางระบายอากาศ ไม่ใช่เปอร์เซ็นต์บรรจุสาย | 30% open area ≠ cable fill | อย่านำ 30% ไปคูณพื้นที่รางเพื่อหาจำนวนสาย | Bangkok Cable Guide PDF p.213 | CLARIFICATION
PV-STD-01 | PV/BESS | ตรวจฉบับ วสท. PV/BESS ปัจจุบันและข้อกำหนดการไฟฟ้าก่อนออกแบบรายละเอียด | วสท. 022013-23 พ.ศ.2568 | ข้อ 5.15 เป็นฐานทั่วไป; วิธีติดตั้ง PV ต้องยืนยันกับมาตรฐานเฉพาะและวิศวกร | EIT official book page | HOLD POINT

## Conduit Data
Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data | Panasonic IMC - Manufacturer Catalogue Data
Brand | Series / type | Item No. | Trade size (inch) | Outside diameter (mm) | Minimum wall thickness (mm) | Length (mm) | Nominal weight (kg/pc) | Primary bundle (pcs) | Master bundle (pcs) | ID_screening (mm) | Area_screening (mm2) | Confirmed actual ID (mm) | Confirmed internal area (mm2) | Standard / listing | Source page | Status / remark
Panasonic | White Conduit IMC | DWM012Y | 1/2 | 20.7 | 1.79 | 3030 | 2.85 | 10 | 300 | 17.12 | 230.1958 | 17.12 | 230.1958 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM034Y | 3/4 | 26.14 | 1.9 | 3030 | 3.94 | 5 | 250 | 22.34 | 391.9731 | 22.34 | 391.9731 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM100Y | 1 | 32.77 | 2.16 | 3025 | 5.23 | 5 | 125 | 28.45 | 635.7032 | 28.45 | 635.7032 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM114Y | 1-1/4 | 41.59 | 2.16 | 3025 | 7.48 | 3 | 75 | 37.27 | 1090.9596 | 37.27 | 1090.9596 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM112Y | 1-1/2 | 47.81 | 2.29 | 3025 | 8.67 | 3 | 75 | 43.23 | 1467.7779 | 43.23 | 1467.7779 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM200Y | 2 | 59.93 | 2.41 | 3025 | 11.65 |  | 50 | 55.11 | 2385.3423 | 55.11 | 2385.3423 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM212Y | 2-1/2 | 72.56 | 3.56 | 3010 | 18.71 |  | 40 | 65.44 | 3363.3841 | 65.44 | 3363.3841 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM300Y | 3 | 88.29 | 3.56 | 3010 | 22.87 |  | 30 | 81.17 | 5174.6499 | 81.17 | 5174.6499 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM312Y | 3-1/2 | 100.86 | 3.56 | 3005 | 26.43 |  | 20 | 93.74 | 6901.441 | 93.74 | 6901.441 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID
Panasonic | White Conduit IMC | DWM400Y | 4 | 113.4 | 3.56 | 3005 | 29.84 |  | 15 | 106.28 | 8871.4166 | 106.28 | 8871.4166 | UL 1242; catalogue also shows TIS 770 coverage | PDF page 5 (printed pp. 7-8) | OPEN - confirm current product/certificate and actual ID

## Ladder Data
KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder | KJL KLSG - Hot-Dip Galvanized Cable Ladder
Brand | Model code | Nominal width W (mm) | Nominal height H (mm) | Length L (mm) | Steel thickness (mm) | Material | Finish | Coating thickness stated | Confirmed usable width (mm) | Confirmed usable depth (mm) | Usable area if adopted (mm2) | Support span/load rating | Source page | Status | Remark
KJL | KLSG 0200 | 200 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0300 | 300 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0400 | 400 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0500 | 500 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0600 | 600 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0700 | 700 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0800 | 800 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 0900 | 900 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.
KJL | KLSG 1000 | 1000 | 100 | 3000 | 2 | SPHC hot rolled mild steel sheet | Hot-Dip Galvanized per catalogue | Average 45-60 micron |  |  |  | TO BE CONFIRMED | PDF pages 122-123 | OPEN | Nominal dimensions are not treated as confirmed usable dimensions.

## Vendor Register
PV Cable OD Master ¦ editable manufacturer input linked to containment sheets
Cable ID | Manufacturer | Cable type | CSA (mm²) | OD input (mm) | Active downstream | OD source / note
PV-PD-4 | Phelps Dodge | H1Z2Z2-K | 4 | 6 | YES | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; conservative max OD used for screening
PV-PD-6 | Phelps Dodge | H1Z2Z2-K | 6 | 7 | YES | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; conservative max OD used for screening | สาย 6 จาก 6.5 -> 7
PV-PD-10 | Phelps Dodge | H1Z2Z2-K | 10 | 8.2 | YES | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; conservative max OD used for screening
PV-PD-16 | Phelps Dodge | H1Z2Z2-K | 16 | 9.8 | YES | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; conservative max OD used for screening
PV-BK-4 | Bangkok Cable | H1Z2Z2-K | 4 | 6.6 | OPTION | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; conservative max OD used for screening
PV-BK-6 | Bangkok Cable | H1Z2Z2-K | 6 | 7.4 | OPTION | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; conservative max OD used for screening
PV-BK-10 | Bangkok Cable | H1Z2Z2-K | 10 | 8.8 | OPTION | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; conservative max OD used for screening
PV-BK-16 | Bangkok Cable | H1Z2Z2-K | 16 | 10.1 | OPTION | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf; conservative max OD used for screening
Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register | Owner Vendor List Verification & Reference Datasheet Register
Category | Brands in attachment | Reference brand | Reference model/document | Local file | Official source | Review status | Design/procurement note
PV Mounting Structure | Goomax; Chiko; Reddot; Sunforson | Chiko | 7Rail | Datasheet/Vendor_Reference/CHIKO_7Rail_Data_Sheet.pdf | https://www.chikolar.com/ | REFERENCE SCREENED | Exact roof interface, wind load and structural calculation remain project-specific
PV MDB Panel | Precise; Mitsubishi; CPT; Asefa; PMK; Sangchai | — | — | — | — | GAP | Need exact assembly datasheet, IEC 61439 evidence, Icw/Icc, IP, form, busbar and SLD
Weather Sensor | Kipp & Zonen; Hukseflux; Rika; Ingenieurburo | Kipp & Zonen | SMP10x/SMP22x | Datasheet/Vendor_Reference/KippZonen_SMP10x_SMP22x_Datasheet_2025.pdf | https://www.kippzonen.com/ | REFERENCE SCREENED | Select sensor class, output, heating and logger compatibility
Protective Relay | Schneider; Siemens; ABB | Schneider | PowerLogic P3 | Datasheet/Vendor_Reference/Schneider_PowerLogic_P3_Catalog_2024.pdf | https://www.se.com/ | REFERENCE SCREENED | Utility protection functions/settings and CT/VT inputs TBC
Power Meter | Janitza; Schneider; ISKRA | Schneider | PowerLogic PM5000 | Datasheet/Vendor_Reference/Schneider_PM5000_Technical_Datasheet.pdf | https://www.se.com/in/en/download/document/29364262/ | REFERENCE SCREENED | Choose exact PM5xxx model, accuracy class, CT input and protocol
Revenue Meter | EDMI; Landis & Gyr | EDMI | Mk10E | Datasheet/Vendor_Reference/EDMI_Mk10E_Factsheet_Rev02_2025.pdf | https://www.edmi-meters.com/ | REFERENCE SCREENED | Final model and utility approval mandatory
PV Connector | Stäubli (MC) | Stäubli | MC4-Evo 2 | Datasheet/Vendor_Reference/Staubli_MC4-Evo2_Cable_Coupler.pdf | https://www.staubli.com/ | REFERENCE SCREENED | Do not cross-mate unlike brands/models; verify cable OD, crimp tool and certification
PV Cable | Thai Wonderful; Phelps Dodge; Prysmian; Bangkok Cable | Phelps Dodge / Bangkok Cable | H1Z2Z2-K | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf; Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf | https://www.pdcable.com/; https://www.bangkokcable.com/ | SOURCE TRANSFERRED | OD master below is the linked design input for the new containment views; confirm exact project product code before IFC.
AC Cable | Bangkok Cable; Thai Yazaki; Phelps Dodge | Phelps Dodge | CV / CV-FD family | Datasheet/Vendor_Reference/Phelps_Dodge_LV_Power_Control_Cables.pdf | https://www.pdcable.com/product/cv-fd-1/ | REFERENCE SCREENED | Exact FD-CV construction, cores, OD, fire certificate and current rating TBC
Communication Cable | LINK; Belden | Belden | 3106A RS-485 | Datasheet/Vendor_Reference/Belden_3106A_RS485_TechData.pdf | https://www.belden.com/ | REFERENCE SCREENED | Confirm protocol, shield grounding, UV/LSZH/fire requirements and separation
Transformer | QTC; Charoenchai; Tirathai; Ekarat | QTC | Oil/dry type family | — | https://qtc-energy.com/transformer-bu/ | WEB REFERENCE ONLY | Need project kVA, HV/LV, vector group, impedance, loss class, enclosure and utility approval
Circuit Breaker | Schneider; Siemens; ABB; Mitsubishi; Fuji | Schneider | ComPacT NSX | Datasheet/Vendor_Reference/Schneider_ComPacT_NSX_Catalog.pdf | https://www.se.com/ | REFERENCE SCREENED | Select exact frame/trip unit, Icu/Ics, DC suitability and coordination
Water Pump | Ebara; Mitsubishi; Grundfos | Grundfos | CR/CRI/CRN | Datasheet/Vendor_Reference/Grundfos_CR_CRI_CRN_Data_Booklet.pdf | https://www.grundfos.com/ | REFERENCE SCREENED | Hydraulic duty, water quality, motor voltage and control TBC
PV Module (additional) | Not listed in attachment | LONGi | Hi-MO 9 HydroClear LR8-66HYD | Datasheet/Vendor_Reference/LONGi_Hi-MO9_HydroClear_LR8-66HYD_635-670M_2026.pdf | https://www.longi.com/ | OUTSIDE VENDOR LIST | Reference only; owner/vendor approval and project string design required
PV Inverter (additional) | Not listed in attachment | Sungrow | SG125CX-P2 | Datasheet/Vendor_Reference/Sungrow_SG125CX-P2_Datasheet_V12.pdf | https://www.sungrowpower.com/ | OUTSIDE VENDOR LIST | Reference only; utility grid code, MPPT/string limits and protection settings required
Jinko PV Module Datasheet ¦ Selected 725 Wp reference from Workspace
Parameter | Value | Unit | Source / engineering note
Manufacturer | Jinko Solar | — | Workspace datasheet
Model | JKM700-725N-66HL5-BDV-Z2C2-OC | — | Workspace datasheet
Selected Pmax | 725 | Wp | Use 725 Wp STC row
Vmp at STC | 41 | V | Workspace datasheet
Imp at STC | 17.69 | A | Workspace datasheet
Voc at STC | 49.2 | V | Workspace datasheet
Isc at STC | 18.74 | A | Workspace datasheet
Max system voltage | 1500 | V DC | Workspace datasheet
Max series fuse | 35 | A | Workspace datasheet
Minimum cell temperature used in design screens | 10 | °C | Project design input; verify inverter/system design
Source file | 3.2.panel_datasheet_JKM700-725N-66HL5-BDV-Z2C2-OC.pdf | — | Workspace file; verify controlled revision before IFC

## Thermal Check (เลือกสาย)
Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill | Thermal / Ampacity Check - Separate from Physical Fill
Three simulated examples are populated below. Base ampacity is taken from the local PV cable datasheet working data; factors are explicit inputs and must be replaced by the project installation calculation.
Circuit ID | Cable model / size | Design current (A) | Base ampacity (A) | Ambient factor | Grouping factor | Other factor | Adjusted ampacity (A) | Result | Ampacity table source | Installation method | Remark
CIR-EX-001 | Phelps Dodge H1Z2Z2-K 4 mm² | 17.69 | 55 | 0.95 | 0.95 | 1 | 49.6375 | PASS | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf | wireway / ventilated | Example 1; replace with project method
CIR-EX-002 | Phelps Dodge H1Z2Z2-K 6 mm² | 17.69 | 70 | 0.95 | 0.9 | 1 | 59.85 | PASS | Phelps_Dodge_PV_Cable_H1Z2Z2-K_Datasheet.pdf | wireway / ventilated | Example 2; replace with project method
CIR-EX-003 | Bangkok Cable H1Z2Z2-K 16 mm² | 100 | 132 | 0.8 | 0.8 | 1 | 84.48 | FAIL | Bangkok_Cable_H1Z2Z2-K_PV_Cable_Datasheet.pdf | wireway / ventilated | Example 3 intentionally demonstrates CHECK
CIR-004 | [7 empty] | REVIEW
CIR-005 | [7 empty] | REVIEW
CIR-006 | [7 empty] | REVIEW
CIR-007 | [7 empty] | REVIEW
CIR-008 | [7 empty] | REVIEW
CIR-009 | [7 empty] | REVIEW
CIR-010 | [7 empty] | REVIEW
CIR-011 | [7 empty] | REVIEW
CIR-012 | [7 empty] | REVIEW
CIR-013 | [7 empty] | REVIEW
CIR-014 | [7 empty] | REVIEW
CIR-015 | [7 empty] | REVIEW
CIR-016 | [7 empty] | REVIEW
CIR-017 | [7 empty] | REVIEW
CIR-018 | [7 empty] | REVIEW
CIR-019 | [7 empty] | REVIEW
CIR-020 | [7 empty] | REVIEW
*ตรวจสอบ Spec. สายไฟว่าเพียงพอหรือไม่

## 1.IMC Max Count
Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening | Maximum Cable Count in Panasonic IMC - EIT Physical Fill Screening
Rev.4: IMC fill screening is governed by the number of cable pieces (Qty). Cores/cable is informational only. The left matrix gives maximum Qty by IMC size; the right matrix uses that left Qty to show total fill %. Actual certified IMC ID is required before IFC. | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks | วสท. 022001-22 ตาราง 5-3: 1 เส้น 53%, 2 เส้น 31%, 3 เส้นขึ้นไป 40%. ตารางนี้แสดงจำนวนสาย/เคเบิลเป็นชิ้น ไม่ใช่จำนวนวงจร และยังไม่รวม ampacity/grouping/bending/pulling checks
IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น | IMC internal ID เป็น screening = Panasonic catalogue OD - 2 x minimum wall thickness; ต้องเปลี่ยนเป็น actual certified ID ก่อน issue design. ค่า 0 = ใส่ไม่ได้ตาม physical fill ของท่อขนาดนั้น
Qty 1 = 53%, Qty 2 = 31%, Qty 3 or more = 40%
Panasonic IMC trade size | Panasonic IMC trade size | Panasonic IMC trade size | Panasonic IMC trade size | Panasonic IMC trade size | Panasonic IMC trade size | 1/2 in | 3/4 in | 1 in | 1-1/4 in | 1-1/2 in | 2 in | 2-1/2 in | 3 in | 3-1/2 in | 4 in | Added comparison: total fill at the maximum Qty from the left matrix
Screening internal ID (mm) | Screening internal ID (mm) | Screening internal ID (mm) | Screening internal ID (mm) | Screening internal ID (mm) | Screening internal ID (mm) | 17.12 | 22.34 | 28.45 | 37.27 | 43.23 | 55.11 | 65.44 | 81.17 | 93.74 | 106.28 |  | Formula = left-table Qty × cable area / IMC internal area. This is the full fill percentage for the Qty shown in the left table, not a one-cable ratio.
Internal area (mm²) | Internal area (mm²) | Internal area (mm²) | Internal area (mm²) | Internal area (mm²) | Internal area (mm²) | 230.1958 | 391.9731 | 635.7032 | 1090.9596 | 1467.7779 | 2385.3423 | 3363.3841 | 5174.6499 | 6901.441 | 8871.4166
System | Cable family | Cores / cable (info.) | CSA mm² | OD mm | Cable area mm² | 1/2 in | 3/4 in | 1 in | 1-1/4 in | 1-1/2 in | 2 in | 2-1/2 in | 3 in | 3-1/2 in | 4 in | Cable / row | 1/2 in | 3/4 in | 1 in | 1-1/4 in | 1-1/2 in | 2 in | 2-1/2 in | 3 in | 3-1/2 in | 4 in
PV | Phelps Dodge H1Z2Z2-K 4 mm² | 1 | 4 | 6 | 28.2743 | 3 | 5 | 8 | 15 | 20 | 33 | 47 | 73 | 97 | 125 | Phelps Dodge H1Z2Z2-K 4 mm² | 36.85% | 36.07% | 35.58% | 38.88% | 38.53% | 39.12% | 39.51% | 39.89% | 39.74% | 39.84%
PV | Phelps Dodge H1Z2Z2-K 6 mm² | 1 | 6 | 7 | 38.4845 | 1 | 4 | 6 | 11 | 15 | 24 | 34 | 53 | 71 | 92 | Phelps Dodge H1Z2Z2-K 6 mm² | 16.72% | 39.27% | 36.32% | 38.8% | 39.33% | 38.72% | 38.9% | 39.42% | 39.59% | 39.91%
PV | Phelps Dodge H1Z2Z2-K 10 mm² | 1 | 10 | 8.2 | 52.8102 | 1 | 2 | 4 | 8 | 11 | 18 | 25 | 39 | 52 | 67 | Phelps Dodge H1Z2Z2-K 10 mm² | 22.94% | 26.95% | 33.23% | 38.73% | 39.58% | 39.85% | 39.25% | 39.8% | 39.79% | 39.88%
PV | Phelps Dodge H1Z2Z2-K 16 mm² | 1 | 16 | 9.8 | 75.4296 | 1 | 1 | 3 | 5 | 7 | 12 | 17 | 27 | 36 | 47 | Phelps Dodge H1Z2Z2-K 16 mm² | 32.77% | 19.24% | 35.6% | 34.57% | 35.97% | 37.95% | 38.13% | 39.36% | 39.35% | 39.96%
AC | Phelps Dodge CV/CV-FD-1C ¦ 25 mm² | 1 | 25 | 12 | 113.0973 | 1 | 1 | 1 | 3 | 5 | 8 | 11 | 18 | 24 | 31 |  | 49.13% | 28.85% | 17.79% | 31.1% | 38.53% | 37.93% | 36.99% | 39.34% | 39.33% | 39.52%
AC | Phelps Dodge CV/CV-FD-1C ¦ 35 mm² | 1 | 35 | 13 | 132.7323 | 0 | 1 | 1 | 3 | 4 | 7 | 10 | 15 | 20 | 26 |  | 0% | 33.86% | 20.88% | 36.5% | 36.17% | 38.95% | 39.46% | 38.48% | 38.47% | 38.9%
AC | Phelps Dodge CV/CV-FD-1C ¦ 50 mm² | 1 | 50 | 15 | 176.7146 | 0 | 1 | 1 | 1 | 3 | 5 | 7 | 11 | 15 | 20 |  | 0% | 45.08% | 27.8% | 16.2% | 36.12% | 37.04% | 36.78% | 37.57% | 38.41% | 39.84%
AC | Phelps Dodge CV/CV-FD-1C ¦ 70 mm² | 1 | 70 | 16 | 201.0619 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 10 | 13 | 17 |  | 0% | 51.29% | 31.63% | 18.43% | 27.4% | 33.72% | 35.87% | 38.86% | 37.87% | 38.53%
AC | Phelps Dodge CV/CV-FD-1C ¦ 95 mm² | 1 | 95 | 18 | 254.469 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 8 | 10 | 13 |  | 0% | 0% | 40.03% | 23.33% | 17.34% | 32% | 37.83% | 39.34% | 36.87% | 37.29%
AC | Phelps Dodge CV/CV-FD-1C ¦ 120 mm² | 1 | 120 | 20 | 314.1593 | 0 | 0 | 1 | 1 | 1 | 3 | 4 | 6 | 8 | 11 |  | 0% | 0% | 49.42% | 28.8% | 21.4% | 39.51% | 37.36% | 36.43% | 36.42% | 38.95%
AC | Phelps Dodge CV/CV-FD-1C ¦ 150 mm² | 1 | 150 | 22 | 380.1327 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 7 | 9 |  | 0% | 0% | 0% | 34.84% | 25.9% | 15.94% | 33.91% | 36.73% | 38.56% | 38.56%
AC | Phelps Dodge CV/CV-FD-1C ¦ 185 mm² | 1 | 185 | 24 | 452.3893 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 7 |  | 0% | 0% | 0% | 41.47% | 30.82% | 18.97% | 26.9% | 34.97% | 39.33% | 35.7%
AC | Phelps Dodge CV/CV-FD-1C ¦ 240 mm² | 1 | 240 | 27 | 572.5553 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 4 | 6 |  | 0% | 0% | 0% | 52.48% | 39.01% | 24% | 17.02% | 33.19% | 33.18% | 38.72%
AC | Phelps Dodge CV/CV-FD-1C ¦ 300 mm² | 1 | 300 | 30 | 706.8583 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 5 |  | 0% | 0% | 0% | 0% | 48.16% | 29.63% | 21.02% | 27.32% | 30.73% | 39.84%
AC | Phelps Dodge CV/CV-FD-1C ¦ 400 mm² | 1 | 400 | 33 | 855.2986 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 4 |  | 0% | 0% | 0% | 0% | 0% | 35.86% | 25.43% | 16.53% | 37.18% | 38.56%
AC | Phelps Dodge CV/CV-FD-1C ¦ 500 mm² | 1 | 500 | 37 | 1075.2101 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 |  | 0% | 0% | 0% | 0% | 0% | 45.08% | 31.97% | 20.78% | 15.58% | 36.36%
AC | Phelps Dodge CV/CV-FD-1C ¦ 630 mm² | 1 | 630 | 41 | 1320.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 |  | 0% | 0% | 0% | 0% | 0% | 0% | 39.25% | 25.51% | 19.13% | 29.76%
AC | Phelps Dodge CV/CV-FD-2C ¦ 10 mm² | 2 | 10 | 16 | 201.0619 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 10 | 13 | 17 |  | 0% | 51.29% | 31.63% | 18.43% | 27.4% | 33.72% | 35.87% | 38.86% | 37.87% | 38.53%
AC | Phelps Dodge CV/CV-FD-2C ¦ 16 mm² | 2 | 16 | 18 | 254.469 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 8 | 10 | 13 |  | 0% | 0% | 40.03% | 23.33% | 17.34% | 32% | 37.83% | 39.34% | 36.87% | 37.29%
AC | Phelps Dodge CV/CV-FD-2C ¦ 25 mm² | 2 | 25 | 21 | 346.3606 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 5 | 7 | 10 |  | 0% | 0% | 0% | 31.75% | 23.6% | 29.04% | 30.89% | 33.47% | 35.13% | 39.04%
AC | Phelps Dodge CV/CV-FD-2C ¦ 35 mm² | 2 | 35 | 23 | 415.4756 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 4 | 6 | 8 |  | 0% | 0% | 0% | 38.08% | 28.31% | 17.42% | 37.06% | 32.12% | 36.12% | 37.47%
AC | Phelps Dodge CV/CV-FD-2C ¦ 50 mm² | 2 | 50 | 25 | 490.8739 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 4 | 5 | 7 |  | 0% | 0% | 0% | 44.99% | 33.44% | 20.58% | 29.19% | 37.94% | 35.56% | 38.73%
AC | Phelps Dodge CV/CV-FD-2C ¦ 70 mm² | 2 | 70 | 30 | 706.8583 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 5 |  | 0% | 0% | 0% | 0% | 48.16% | 29.63% | 21.02% | 27.32% | 30.73% | 39.84%
AC | Phelps Dodge CV/CV-FD-2C ¦ 95 mm² | 2 | 95 | 33 | 855.2986 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 4 |  | 0% | 0% | 0% | 0% | 0% | 35.86% | 25.43% | 16.53% | 37.18% | 38.56%
AC | Phelps Dodge CV/CV-FD-2C ¦ 120 mm² | 2 | 120 | 37 | 1075.2101 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 |  | 0% | 0% | 0% | 0% | 0% | 45.08% | 31.97% | 20.78% | 15.58% | 36.36%
AC | Phelps Dodge CV/CV-FD-2C ¦ 150 mm² | 2 | 150 | 41 | 1320.2543 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 |  | 0% | 0% | 0% | 0% | 0% | 0% | 39.25% | 25.51% | 19.13% | 29.76%
AC | Phelps Dodge CV/CV-FD-2C ¦ 185 mm² | 2 | 185 | 45 | 1590.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 47.29% | 30.74% | 23.04% | 17.93%
AC | Phelps Dodge CV/CV-FD-2C ¦ 240 mm² | 2 | 240 | 51 | 2042.8206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 39.48% | 29.6% | 23.03%
AC | Phelps Dodge CV/CV-FD-2C ¦ 300 mm² | 2 | 300 | 55 | 2375.8294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 45.91% | 34.43% | 26.78%
AC | Phelps Dodge CV/CV-FD-2C ¦ 400 mm² | 2 | 400 | 62 | 3019.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 43.75% | 34.03%
AC | Phelps Dodge CV/CV-FD-3C ¦ 10 mm² | 3 | 10 | 16 | 201.0619 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 10 | 13 | 17 |  | 0% | 51.29% | 31.63% | 18.43% | 27.4% | 33.72% | 35.87% | 38.86% | 37.87% | 38.53%
AC | Phelps Dodge CV/CV-FD-3C ¦ 16 mm² | 3 | 16 | 18 | 254.469 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 8 | 10 | 13 |  | 0% | 0% | 40.03% | 23.33% | 17.34% | 32% | 37.83% | 39.34% | 36.87% | 37.29%
AC | Phelps Dodge CV/CV-FD-3C ¦ 25 mm² | 3 | 25 | 22 | 380.1327 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 7 | 9 |  | 0% | 0% | 0% | 34.84% | 25.9% | 15.94% | 33.91% | 36.73% | 38.56% | 38.56%
AC | Phelps Dodge CV/CV-FD-3C ¦ 35 mm² | 3 | 35 | 24 | 452.3893 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 7 |  | 0% | 0% | 0% | 41.47% | 30.82% | 18.97% | 26.9% | 34.97% | 39.33% | 35.7%
AC | Phelps Dodge CV/CV-FD-3C ¦ 50 mm² | 3 | 50 | 27 | 572.5553 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 4 | 6 |  | 0% | 0% | 0% | 52.48% | 39.01% | 24% | 17.02% | 33.19% | 33.18% | 38.72%
AC | Phelps Dodge CV/CV-FD-3C ¦ 70 mm² | 3 | 70 | 32 | 804.2477 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 4 |  | 0% | 0% | 0% | 0% | 0% | 33.72% | 23.91% | 15.54% | 34.96% | 36.26%
AC | Phelps Dodge CV/CV-FD-3C ¦ 95 mm² | 3 | 95 | 36 | 1017.876 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 |  | 0% | 0% | 0% | 0% | 0% | 42.67% | 30.26% | 19.67% | 29.5% | 34.42%
AC | Phelps Dodge CV/CV-FD-3C ¦ 120 mm² | 3 | 120 | 39 | 1194.5906 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 |  | 0% | 0% | 0% | 0% | 0% | 50.08% | 35.52% | 23.09% | 17.31% | 26.93%
AC | Phelps Dodge CV/CV-FD-3C ¦ 150 mm² | 3 | 150 | 43 | 1452.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 43.18% | 28.06% | 21.04% | 16.37%
AC | Phelps Dodge CV/CV-FD-3C ¦ 185 mm² | 3 | 185 | 48 | 1809.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.97% | 26.22% | 20.4%
AC | Phelps Dodge CV/CV-FD-3C ¦ 240 mm² | 3 | 240 | 54 | 2290.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 44.26% | 33.18% | 25.82%
AC | Phelps Dodge CV/CV-FD-3C ¦ 300 mm² | 3 | 300 | 59 | 2733.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 52.83% | 39.61% | 30.82%
AC | Phelps Dodge CV/CV-FD-3C ¦ 400 mm² | 3 | 400 | 66 | 3421.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 49.57% | 38.56%
AC | Phelps Dodge CV/CV-FD-4C ¦ 10 mm² | 4 | 10 | 18 | 254.469 | 0 | 0 | 1 | 1 | 1 | 3 | 5 | 8 | 10 | 13 |  | 0% | 0% | 40.03% | 23.33% | 17.34% | 32% | 37.83% | 39.34% | 36.87% | 37.29%
AC | Phelps Dodge CV/CV-FD-4C ¦ 16 mm² | 4 | 16 | 20 | 314.1593 | 0 | 0 | 1 | 1 | 1 | 3 | 4 | 6 | 8 | 11 |  | 0% | 0% | 49.42% | 28.8% | 21.4% | 39.51% | 37.36% | 36.43% | 36.42% | 38.95%
AC | Phelps Dodge CV/CV-FD-4C ¦ 25 mm² | 4 | 25 | 24 | 452.3893 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 4 | 6 | 7 |  | 0% | 0% | 0% | 41.47% | 30.82% | 18.97% | 26.9% | 34.97% | 39.33% | 35.7%
AC | Phelps Dodge CV/CV-FD-4C ¦ 35 mm² | 4 | 35 | 27 | 572.5553 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3 | 4 | 6 |  | 0% | 0% | 0% | 52.48% | 39.01% | 24% | 17.02% | 33.19% | 33.18% | 38.72%
AC | Phelps Dodge CV/CV-FD-4C ¦ 50 mm² | 4 | 50 | 30 | 706.8583 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 5 |  | 0% | 0% | 0% | 0% | 48.16% | 29.63% | 21.02% | 27.32% | 30.73% | 39.84%
AC | Phelps Dodge CV/CV-FD-4C ¦ 70 mm² | 4 | 70 | 35 | 962.1128 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 3 |  | 0% | 0% | 0% | 0% | 0% | 40.33% | 28.61% | 18.59% | 27.88% | 32.54%
AC | Phelps Dodge CV/CV-FD-4C ¦ 95 mm² | 4 | 95 | 39 | 1194.5906 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 |  | 0% | 0% | 0% | 0% | 0% | 50.08% | 35.52% | 23.09% | 17.31% | 26.93%
AC | Phelps Dodge CV/CV-FD-4C ¦ 120 mm² | 4 | 120 | 43 | 1452.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 43.18% | 28.06% | 21.04% | 16.37%
AC | Phelps Dodge CV/CV-FD-4C ¦ 150 mm² | 4 | 150 | 48 | 1809.5574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 34.97% | 26.22% | 20.4%
AC | Phelps Dodge CV/CV-FD-4C ¦ 185 mm² | 4 | 185 | 53 | 2206.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 42.63% | 31.97% | 24.87%
AC | Phelps Dodge CV/CV-FD-4C ¦ 240 mm² | 4 | 240 | 60 | 2827.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.97% | 31.87%
AC | Phelps Dodge CV/CV-FD-4C ¦ 300 mm² | 4 | 300 | 66 | 3421.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 49.57% | 38.56%
AC | Phelps Dodge CV/CV-FD-4C ¦ 400 mm² | 4 | 400 | 74 | 4300.8403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 48.48%
กำหนดจากขนาดราง Wireway และดู MAX
User-entry IMC cable mix ¦ total cable area vs WST fill condition
Enter cable type/CSA/OD/Qty per row. WST allowed fill uses TOTAL Qty in the mix: Qty 1 = 53%, Qty 2 = 31%, Qty 3 or more = 40%. Cores/cable is informational only.
Line | Cable type / model | Cores / cable (info.) | CSA (mm²) | OD (mm) | Qty | Area / cable (mm²) | Total cable area (mm²) | IMC trade size | IMC internal area (mm²) | WST allowed fill (total Qty) | Fill % = total cable area / conduit area | WST match | Engineering result | Engineering note
USER-001 | Phelps Dodge CV/CV-FD-1C ¦ 95 mm² | 1 | 4 | 18 | 4 | 254.469 | 1017.876 | 1/2 in | 230.1958 | 40% | 442.2% | FAIL | CHECK | Example; total Qty rule; confirm exact OD and certified IMC ID
USER-002 |  | 1 | 6 | 0 | 0 | 0 | 0 | 1/2 in | 230.1958 | 40% | 0% | PASS | USE / PASS | Example; total Qty rule; confirm exact OD and certified IMC ID
USER-003 |  | 1 | 10 | 0 | 0 | 0 | 0 | 3/4 in | 391.9731 | 40% | 0% | PASS | USE / PASS | Example; total Qty rule; confirm exact OD and certified IMC ID
USER-004 |  | 2 | 16 | 0 | 0 | 0 | 0 | 1 in | 635.7032 | 40% | 0% | PASS | USE / PASS | Example; cores/cable shown only for information
USER-005 | AC Cable (THW) - G 50 sq.mm. | 1 | 25 | 12.8 | 1 | 128.6796 | 128.6796 | 1 in | 635.7032 | 53% | 20.24% | PASS | USE / PASS | Free user-entry row; total Qty rule applies
TOTAL ENTERED MIX |  |  |  |  | 5 |  | 1146.5557 |  |  |  |  | SEE SUMMARY BELOW
IMC selection recommendation ¦ linked to TOTAL Qty and TOTAL cable area above
The summary checks one common IMC for the entire entered mix. If no single IMC passes, the parallel-conduit column gives the minimum number of equal conduits using the same Qty-based WST fill rule.
Total Qty | Total cable area (mm²) | Qty-based WST fill | Minimum internal area required (mm²) | Recommended single IMC | Single fill % | Single result | Recommendation
5 | 1146.5557 | 40% | 2866.3891 | 2-1/2 in | 34.09% | PASS | Single conduit passes
IMC trade size | Internal area (mm²) | Total Qty | WST allowed fill | Single fill % | Single status | Minimum parallel conduits | Fill / conduit | Recommendation if parallel
1/2 in | 230.1958 | 5 | 40% | 498.1% | FAIL | 13 | 38.31% | 13 parallel conduits
3/4 in | 391.9731 | 5 | 40% | 292.5% | FAIL | 8 | 36.56% | 8 parallel conduits
1 in | 635.7032 | 5 | 40% | 180.4% | FAIL | 5 | 36.07% | 5 parallel conduits
1-1/4 in | 1090.9596 | 5 | 40% | 105.1% | FAIL | 3 | 35.03% | 3 parallel conduits
1-1/2 in | 1467.7779 | 5 | 40% | 78.12% | FAIL | 2 | 39.06% | 2 parallel conduits
2 in | 2385.3423 | 5 | 40% | 48.07% | FAIL | 2 | 24.03% | 2 parallel conduits
2-1/2 in | 3363.3841 | 5 | 40% | 34.09% | PASS | 1 | 34.09% | Single conduit passes
3 in | 5174.6499 | 5 | 40% | 22.16% | PASS | 1 | 22.16% | Single conduit passes
3-1/2 in | 6901.441 | 5 | 40% | 16.61% | PASS | 1 | 16.61% | Single conduit passes
4 in | 8871.4166 | 5 | 40% | 12.92% | PASS | 1 | 12.92% | Single conduit passes
[9 empty] | AC Cable (THW) - G 240 sq.mm. |  | 26.6
[9 empty] | AC Cable (THW) - G 185 sq.mm. |  | 23.3
[9 empty] | AC Cable (THW) - G 120 sq.mm. |  | 18.8
[9 empty] | AC Cable (THW) - G 95 sq.mm. |  | 17.1
[9 empty] | AC Cable (THW) - G 70 sq.mm. |  | 14.6
[9 empty] | AC Cable (THW) - G 50 sq.mm. |  | 12.8
[9 empty] | AC Cable (THW) - G 35 sq.mm. |  | 10.9
[9 empty] | AC Cable (THW) - G 25 sq.mm. |  | 9.7
[9 empty] | AC Cable (THW) - G 16 sq.mm. |  | 7.8
[9 empty] | AC Cable (THW) - G 10 sq.mm. |  | 6.7
[9 empty] | AC Cable (THW) - G 6 sq.mm. |  | 5.2

## 2.Ladder-(AC)
Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening | Maximum Single-Layer Cable Count on KJL Ladder - EIT Eligibility Screening
วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width | วสท. 022001-22 ข้อ 5.15: วางชั้นเดียว/trefoil; สาย 1C มีเปลือกต้องไม่น้อยกว่า 25 mm²; multicore ใช้ได้ตามเงื่อนไข. จำนวนคำนวณจาก W >= 1.25 x ΣD (25% reserve) และ nominal KJL width
PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41 | PV 1C 4/6 mm² และ AC 1C 10/16 mm² = NOT PERMITTED DIRECT จึงแสดง 0. ผลอื่นเป็น physical screening; ต้องใช้ usable width จริง, cable cleat/divider, bending, short-circuit forces และ grouping factor ตาราง 5-40/5-41
Nominal ladder width (mm) - replace with usable width | Nominal ladder width (mm) - replace with usable width | Nominal ladder width (mm) - replace with usable width | Nominal ladder width (mm) - replace with usable width | Nominal ladder width (mm) - replace with usable width | Nominal ladder width (mm) - replace with usable width | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | Added comparison: left-table maximum Qty × cable OD / ladder width
System | Cable family | Cores | CSA mm² | OD mm | Direct-on-ladder eligibility | 200 mm | 300 mm | 400 mm | 500 mm | 600 mm | 700 mm | 800 mm | 900 mm | 1000 mm | Cable / row | 200 mm | 300 mm | 400 mm | 500 mm | 600 mm | 700 mm | 800 mm | 900 mm | 1000 mm
AC | Phelps Dodge CV/CV-FD-1C ¦ 10 mm² | 1 | 10 | 10 | NOT PERMITTED DIRECT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Phelps Dodge CV/CV-FD-1C ¦ 10 mm² | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
AC | Phelps Dodge CV/CV-FD-1C ¦ 16 mm² | 1 | 16 | 11 | NOT PERMITTED DIRECT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Phelps Dodge CV/CV-FD-1C ¦ 16 mm² | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
AC | Phelps Dodge CV/CV-FD-1C ¦ 25 mm² | 1 | 25 | 12 | ALLOWED - physical screen | 13 | 20 | 26 | 33 | 40 | 46 | 53 | 60 | 66 | Phelps Dodge CV/CV-FD-1C ¦ 25 mm² | 78% | 80% | 78% | 79.2% | 80% | 78.86% | 79.5% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-1C ¦ 35 mm² | 1 | 35 | 13 | ALLOWED - physical screen | 12 | 18 | 24 | 30 | 36 | 43 | 49 | 55 | 61 | Phelps Dodge CV/CV-FD-1C ¦ 35 mm² | 78% | 78% | 78% | 78% | 78% | 79.86% | 79.62% | 79.44% | 79.3%
AC | Phelps Dodge CV/CV-FD-1C ¦ 50 mm² | 1 | 50 | 15 | ALLOWED - physical screen | 10 | 16 | 21 | 26 | 32 | 37 | 42 | 48 | 53 | Phelps Dodge CV/CV-FD-1C ¦ 50 mm² | 75% | 80% | 78.75% | 78% | 80% | 79.29% | 78.75% | 80% | 79.5%
AC | Phelps Dodge CV/CV-FD-1C ¦ 70 mm² | 1 | 70 | 16 | ALLOWED - physical screen | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | Phelps Dodge CV/CV-FD-1C ¦ 70 mm² | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
AC | Phelps Dodge CV/CV-FD-1C ¦ 95 mm² | 1 | 95 | 18 | ALLOWED - physical screen | 8 | 13 | 17 | 22 | 26 | 31 | 35 | 40 | 44 | Phelps Dodge CV/CV-FD-1C ¦ 95 mm² | 72% | 78% | 76.5% | 79.2% | 78% | 79.71% | 78.75% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-1C ¦ 120 mm² | 1 | 120 | 20 | ALLOWED - physical screen | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | Phelps Dodge CV/CV-FD-1C ¦ 120 mm² | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
AC | Phelps Dodge CV/CV-FD-1C ¦ 150 mm² | 1 | 150 | 22 | ALLOWED - physical screen | 7 | 10 | 14 | 18 | 21 | 25 | 29 | 32 | 36 | Phelps Dodge CV/CV-FD-1C ¦ 150 mm² | 77% | 73.33% | 77% | 79.2% | 77% | 78.57% | 79.75% | 78.22% | 79.2%
AC | Phelps Dodge CV/CV-FD-1C ¦ 185 mm² | 1 | 185 | 24 | ALLOWED - physical screen | 6 | 10 | 13 | 16 | 20 | 23 | 26 | 30 | 33 | Phelps Dodge CV/CV-FD-1C ¦ 185 mm² | 72% | 80% | 78% | 76.8% | 80% | 78.86% | 78% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-1C ¦ 240 mm² | 1 | 240 | 27 | ALLOWED - physical screen | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 26 | 29 | Phelps Dodge CV/CV-FD-1C ¦ 240 mm² | 67.5% | 72% | 74.25% | 75.6% | 76.5% | 77.14% | 77.62% | 78% | 78.3%
AC | Phelps Dodge CV/CV-FD-1C ¦ 300 mm² | 1 | 300 | 30 | ALLOWED - physical screen | 5 | 8 | 10 | 13 | 16 | 18 | 21 | 24 | 26 | Phelps Dodge CV/CV-FD-1C ¦ 300 mm² | 75% | 80% | 75% | 78% | 80% | 77.14% | 78.75% | 80% | 78%
AC | Phelps Dodge CV/CV-FD-1C ¦ 400 mm² | 1 | 400 | 33 | ALLOWED - physical screen | 4 | 7 | 9 | 12 | 14 | 16 | 19 | 21 | 24 | Phelps Dodge CV/CV-FD-1C ¦ 400 mm² | 66% | 77% | 74.25% | 79.2% | 77% | 75.43% | 78.38% | 77% | 79.2%
AC | Phelps Dodge CV/CV-FD-1C ¦ 500 mm² | 1 | 500 | 37 | ALLOWED - physical screen | 4 | 6 | 8 | 10 | 12 | 15 | 17 | 19 | 21 | Phelps Dodge CV/CV-FD-1C ¦ 500 mm² | 74% | 74% | 74% | 74% | 74% | 79.29% | 78.62% | 78.11% | 77.7%
AC | Phelps Dodge CV/CV-FD-1C ¦ 630 mm² | 1 | 630 | 41 | ALLOWED - physical screen | 3 | 5 | 7 | 9 | 11 | 13 | 15 | 17 | 19 | Phelps Dodge CV/CV-FD-1C ¦ 630 mm² | 61.5% | 68.33% | 71.75% | 73.8% | 75.17% | 76.14% | 76.88% | 77.44% | 77.9%
AC | Phelps Dodge CV/CV-FD-2C ¦ 10 mm² | 2 | 10 | 16 | ALLOWED - physical screen | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | Phelps Dodge CV/CV-FD-2C ¦ 10 mm² | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
AC | Phelps Dodge CV/CV-FD-2C ¦ 16 mm² | 2 | 16 | 18 | ALLOWED - physical screen | 8 | 13 | 17 | 22 | 26 | 31 | 35 | 40 | 44 | Phelps Dodge CV/CV-FD-2C ¦ 16 mm² | 72% | 78% | 76.5% | 79.2% | 78% | 79.71% | 78.75% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-2C ¦ 25 mm² | 2 | 25 | 21 | ALLOWED - physical screen | 7 | 11 | 15 | 19 | 22 | 26 | 30 | 34 | 38 | Phelps Dodge CV/CV-FD-2C ¦ 25 mm² | 73.5% | 77% | 78.75% | 79.8% | 77% | 78% | 78.75% | 79.33% | 79.8%
AC | Phelps Dodge CV/CV-FD-2C ¦ 35 mm² | 2 | 35 | 23 | ALLOWED - physical screen | 6 | 10 | 13 | 17 | 20 | 24 | 27 | 31 | 34 | Phelps Dodge CV/CV-FD-2C ¦ 35 mm² | 69% | 76.67% | 74.75% | 78.2% | 76.67% | 78.86% | 77.62% | 79.22% | 78.2%
AC | Phelps Dodge CV/CV-FD-2C ¦ 50 mm² | 2 | 50 | 25 | ALLOWED - physical screen | 6 | 9 | 12 | 16 | 19 | 22 | 25 | 28 | 32 | Phelps Dodge CV/CV-FD-2C ¦ 50 mm² | 75% | 75% | 75% | 80% | 79.17% | 78.57% | 78.12% | 77.78% | 80%
AC | Phelps Dodge CV/CV-FD-2C ¦ 70 mm² | 2 | 70 | 30 | ALLOWED - physical screen | 5 | 8 | 10 | 13 | 16 | 18 | 21 | 24 | 26 | Phelps Dodge CV/CV-FD-2C ¦ 70 mm² | 75% | 80% | 75% | 78% | 80% | 77.14% | 78.75% | 80% | 78%
AC | Phelps Dodge CV/CV-FD-2C ¦ 95 mm² | 2 | 95 | 33 | ALLOWED - physical screen | 4 | 7 | 9 | 12 | 14 | 16 | 19 | 21 | 24 | Phelps Dodge CV/CV-FD-2C ¦ 95 mm² | 66% | 77% | 74.25% | 79.2% | 77% | 75.43% | 78.38% | 77% | 79.2%
AC | Phelps Dodge CV/CV-FD-2C ¦ 120 mm² | 2 | 120 | 37 | ALLOWED - physical screen | 4 | 6 | 8 | 10 | 12 | 15 | 17 | 19 | 21 | Phelps Dodge CV/CV-FD-2C ¦ 120 mm² | 74% | 74% | 74% | 74% | 74% | 79.29% | 78.62% | 78.11% | 77.7%
AC | Phelps Dodge CV/CV-FD-2C ¦ 150 mm² | 2 | 150 | 41 | ALLOWED - physical screen | 3 | 5 | 7 | 9 | 11 | 13 | 15 | 17 | 19 | Phelps Dodge CV/CV-FD-2C ¦ 150 mm² | 61.5% | 68.33% | 71.75% | 73.8% | 75.17% | 76.14% | 76.88% | 77.44% | 77.9%
AC | Phelps Dodge CV/CV-FD-2C ¦ 185 mm² | 2 | 185 | 45 | ALLOWED - physical screen | 3 | 5 | 7 | 8 | 10 | 12 | 14 | 16 | 17 | Phelps Dodge CV/CV-FD-2C ¦ 185 mm² | 67.5% | 75% | 78.75% | 72% | 75% | 77.14% | 78.75% | 80% | 76.5%
AC | Phelps Dodge CV/CV-FD-2C ¦ 240 mm² | 2 | 240 | 51 | ALLOWED - physical screen | 3 | 4 | 6 | 7 | 9 | 10 | 12 | 14 | 15 | Phelps Dodge CV/CV-FD-2C ¦ 240 mm² | 76.5% | 68% | 76.5% | 71.4% | 76.5% | 72.86% | 76.5% | 79.33% | 76.5%
AC | Phelps Dodge CV/CV-FD-2C ¦ 300 mm² | 2 | 300 | 55 | ALLOWED - physical screen | 2 | 4 | 5 | 7 | 8 | 10 | 11 | 13 | 14 | Phelps Dodge CV/CV-FD-2C ¦ 300 mm² | 55% | 73.33% | 68.75% | 77% | 73.33% | 78.57% | 75.62% | 79.44% | 77%
AC | Phelps Dodge CV/CV-FD-2C ¦ 400 mm² | 2 | 400 | 62 | ALLOWED - physical screen | 2 | 3 | 5 | 6 | 7 | 9 | 10 | 11 | 12 | Phelps Dodge CV/CV-FD-2C ¦ 400 mm² | 62% | 62% | 77.5% | 74.4% | 72.33% | 79.71% | 77.5% | 75.78% | 74.4%
AC | Phelps Dodge CV/CV-FD-3C ¦ 10 mm² | 3 | 10 | 16 | ALLOWED - physical screen | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | Phelps Dodge CV/CV-FD-3C ¦ 10 mm² | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
AC | Phelps Dodge CV/CV-FD-3C ¦ 16 mm² | 3 | 16 | 18 | ALLOWED - physical screen | 8 | 13 | 17 | 22 | 26 | 31 | 35 | 40 | 44 | Phelps Dodge CV/CV-FD-3C ¦ 16 mm² | 72% | 78% | 76.5% | 79.2% | 78% | 79.71% | 78.75% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-3C ¦ 25 mm² | 3 | 25 | 22 | ALLOWED - physical screen | 7 | 10 | 14 | 18 | 21 | 25 | 29 | 32 | 36 | Phelps Dodge CV/CV-FD-3C ¦ 25 mm² | 77% | 73.33% | 77% | 79.2% | 77% | 78.57% | 79.75% | 78.22% | 79.2%
AC | Phelps Dodge CV/CV-FD-3C ¦ 35 mm² | 3 | 35 | 24 | ALLOWED - physical screen | 6 | 10 | 13 | 16 | 20 | 23 | 26 | 30 | 33 | Phelps Dodge CV/CV-FD-3C ¦ 35 mm² | 72% | 80% | 78% | 76.8% | 80% | 78.86% | 78% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-3C ¦ 50 mm² | 3 | 50 | 27 | ALLOWED - physical screen | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 26 | 29 | Phelps Dodge CV/CV-FD-3C ¦ 50 mm² | 67.5% | 72% | 74.25% | 75.6% | 76.5% | 77.14% | 77.62% | 78% | 78.3%
AC | Phelps Dodge CV/CV-FD-3C ¦ 70 mm² | 3 | 70 | 32 | ALLOWED - physical screen | 5 | 7 | 10 | 12 | 15 | 17 | 20 | 22 | 25 | Phelps Dodge CV/CV-FD-3C ¦ 70 mm² | 80% | 74.67% | 80% | 76.8% | 80% | 77.71% | 80% | 78.22% | 80%
AC | Phelps Dodge CV/CV-FD-3C ¦ 95 mm² | 3 | 95 | 36 | ALLOWED - physical screen | 4 | 6 | 8 | 11 | 13 | 15 | 17 | 20 | 22 | Phelps Dodge CV/CV-FD-3C ¦ 95 mm² | 72% | 72% | 72% | 79.2% | 78% | 77.14% | 76.5% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-3C ¦ 120 mm² | 3 | 120 | 39 | ALLOWED - physical screen | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | Phelps Dodge CV/CV-FD-3C ¦ 120 mm² | 78% | 78% | 78% | 78% | 78% | 78% | 78% | 78% | 78%
AC | Phelps Dodge CV/CV-FD-3C ¦ 150 mm² | 3 | 150 | 43 | ALLOWED - physical screen | 3 | 5 | 7 | 9 | 11 | 13 | 14 | 16 | 18 | Phelps Dodge CV/CV-FD-3C ¦ 150 mm² | 64.5% | 71.67% | 75.25% | 77.4% | 78.83% | 79.86% | 75.25% | 76.44% | 77.4%
AC | Phelps Dodge CV/CV-FD-3C ¦ 185 mm² | 3 | 185 | 48 | ALLOWED - physical screen | 3 | 5 | 6 | 8 | 10 | 11 | 13 | 15 | 16 | Phelps Dodge CV/CV-FD-3C ¦ 185 mm² | 72% | 80% | 72% | 76.8% | 80% | 75.43% | 78% | 80% | 76.8%
AC | Phelps Dodge CV/CV-FD-3C ¦ 240 mm² | 3 | 240 | 54 | ALLOWED - physical screen | 2 | 4 | 5 | 7 | 8 | 10 | 11 | 13 | 14 | Phelps Dodge CV/CV-FD-3C ¦ 240 mm² | 54% | 72% | 67.5% | 75.6% | 72% | 77.14% | 74.25% | 78% | 75.6%
AC | Phelps Dodge CV/CV-FD-3C ¦ 300 mm² | 3 | 300 | 59 | ALLOWED - physical screen | 2 | 4 | 5 | 6 | 8 | 9 | 10 | 12 | 13 | Phelps Dodge CV/CV-FD-3C ¦ 300 mm² | 59% | 78.67% | 73.75% | 70.8% | 78.67% | 75.86% | 73.75% | 78.67% | 76.7%
AC | Phelps Dodge CV/CV-FD-3C ¦ 400 mm² | 3 | 400 | 66 | ALLOWED - physical screen | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 12 | Phelps Dodge CV/CV-FD-3C ¦ 400 mm² | 66% | 66% | 66% | 79.2% | 77% | 75.43% | 74.25% | 73.33% | 79.2%
AC | Phelps Dodge CV/CV-FD-4C ¦ 10 mm² | 4 | 10 | 18 | ALLOWED - physical screen | 8 | 13 | 17 | 22 | 26 | 31 | 35 | 40 | 44 | Phelps Dodge CV/CV-FD-4C ¦ 10 mm² | 72% | 78% | 76.5% | 79.2% | 78% | 79.71% | 78.75% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-4C ¦ 16 mm² | 4 | 16 | 20 | ALLOWED - physical screen | 8 | 12 | 16 | 20 | 24 | 28 | 32 | 36 | 40 | Phelps Dodge CV/CV-FD-4C ¦ 16 mm² | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
AC | Phelps Dodge CV/CV-FD-4C ¦ 25 mm² | 4 | 25 | 24 | ALLOWED - physical screen | 6 | 10 | 13 | 16 | 20 | 23 | 26 | 30 | 33 | Phelps Dodge CV/CV-FD-4C ¦ 25 mm² | 72% | 80% | 78% | 76.8% | 80% | 78.86% | 78% | 80% | 79.2%
AC | Phelps Dodge CV/CV-FD-4C ¦ 35 mm² | 4 | 35 | 27 | ALLOWED - physical screen | 5 | 8 | 11 | 14 | 17 | 20 | 23 | 26 | 29 | Phelps Dodge CV/CV-FD-4C ¦ 35 mm² | 67.5% | 72% | 74.25% | 75.6% | 76.5% | 77.14% | 77.62% | 78% | 78.3%
AC | Phelps Dodge CV/CV-FD-4C ¦ 50 mm² | 4 | 50 | 30 | ALLOWED - physical screen | 5 | 8 | 10 | 13 | 16 | 18 | 21 | 24 | 26 | Phelps Dodge CV/CV-FD-4C ¦ 50 mm² | 75% | 80% | 75% | 78% | 80% | 77.14% | 78.75% | 80% | 78%
AC | Phelps Dodge CV/CV-FD-4C ¦ 70 mm² | 4 | 70 | 35 | ALLOWED - physical screen | 4 | 6 | 9 | 11 | 13 | 16 | 18 | 20 | 22 | Phelps Dodge CV/CV-FD-4C ¦ 70 mm² | 70% | 70% | 78.75% | 77% | 75.83% | 80% | 78.75% | 77.78% | 77%
AC | Phelps Dodge CV/CV-FD-4C ¦ 95 mm² | 4 | 95 | 39 | ALLOWED - physical screen | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | Phelps Dodge CV/CV-FD-4C ¦ 95 mm² | 78% | 78% | 78% | 78% | 78% | 78% | 78% | 78% | 78%
AC | Phelps Dodge CV/CV-FD-4C ¦ 120 mm² | 4 | 120 | 43 | ALLOWED - physical screen | 3 | 5 | 7 | 9 | 11 | 13 | 14 | 16 | 18 | Phelps Dodge CV/CV-FD-4C ¦ 120 mm² | 64.5% | 71.67% | 75.25% | 77.4% | 78.83% | 79.86% | 75.25% | 76.44% | 77.4%
AC | Phelps Dodge CV/CV-FD-4C ¦ 150 mm² | 4 | 150 | 48 | ALLOWED - physical screen | 3 | 5 | 6 | 8 | 10 | 11 | 13 | 15 | 16 | Phelps Dodge CV/CV-FD-4C ¦ 150 mm² | 72% | 80% | 72% | 76.8% | 80% | 75.43% | 78% | 80% | 76.8%
AC | Phelps Dodge CV/CV-FD-4C ¦ 185 mm² | 4 | 185 | 53 | ALLOWED - physical screen | 3 | 4 | 6 | 7 | 9 | 10 | 12 | 13 | 15 | Phelps Dodge CV/CV-FD-4C ¦ 185 mm² | 79.5% | 70.67% | 79.5% | 74.2% | 79.5% | 75.71% | 79.5% | 76.56% | 79.5%
AC | Phelps Dodge CV/CV-FD-4C ¦ 240 mm² | 4 | 240 | 60 | ALLOWED - physical screen | 2 | 4 | 5 | 6 | 8 | 9 | 10 | 12 | 13 | Phelps Dodge CV/CV-FD-4C ¦ 240 mm² | 60% | 80% | 75% | 72% | 80% | 77.14% | 75% | 80% | 78%
AC | Phelps Dodge CV/CV-FD-4C ¦ 300 mm² | 4 | 300 | 66 | ALLOWED - physical screen | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 12 | Phelps Dodge CV/CV-FD-4C ¦ 300 mm² | 66% | 66% | 66% | 79.2% | 77% | 75.43% | 74.25% | 73.33% | 79.2%
AC | Phelps Dodge CV/CV-FD-4C ¦ 400 mm² | 4 | 400 | 74 | ALLOWED - physical screen | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Phelps Dodge CV/CV-FD-4C ¦ 400 mm² | 74% | 74% | 74% | 74% | 74% | 74% | 74% | 74% | 74%
User-entry ladder cable mix ¦ EIT width screen and direct-on-ladder eligibility
Enter each cable type/cores/CSA/OD/Qty and usable ladder width. EIT width screen is ΣD_cable ≤ 0.8W; direct-on-ladder eligibility is checked separately.
1C <25 mm² is not permitted direct; protected route required | [5 empty] | 4 4: 0.8W
Line | Cable type / model | System | CSA (mm²) | OD (mm) | Qty | Usable ladder width (mm) | ΣD cable (mm) | 0.8W limit (mm) | Width utilization % | EIT width match | Engineering note
USER-AC-001 | Phelps Dodge CV/CV-FD-1C ¦ 25 mm² | AC | 25 | 12 | 10 | 300 | 120 | 240 | 40% | PASS | Allowed cable example; verify cleat/support and actual usable width
USER-AC-002 | Phelps Dodge CV/CV-FD-1C ¦ 70 mm² | AC | 70 | 16 | 25 | 600 | 400 | 480 | 66.67% | PASS | Allowed cable example; verify cleat/support and actual usable width
USER-AC-003 | Phelps Dodge CV/CV-FD-2C ¦ 16 mm² | AC | 16 | 18 | 20 | 500 | 360 | 400 | 72% | PASS | Multicore example; verify cable arrangement and support
USER-AC-004 | Phelps Dodge CV/CV-FD-1C ¦ 10 mm² | AC | 10 | 10 | 10 | 200 | 100 | 160 | 50% | PASS | 1C <25 mm² is not permitted direct; protected route required
USER-AC-005 | Phelps Dodge CV/CV-FD-1C ¦ 35 mm² | AC | 35 | 13 | 20 | 200 | 260 | 160 | 130% | FAIL | Width intentionally above 0.8W to demonstrate CHECK
TOTAL ENTERED MIX | [5 empty] | 3 3: 1240; 4 4: 1440; 7 6: SEE SUMMARY BELOW
Ladder selection summary ¦ based on total ΣD cable from the user-entry mix | bar: 2 2 to 4 4
The common-width screen uses ΣD cable ≤ 0.8W. If the required width exceeds 1,000 mm, the result recommends parallel ladder routes. | bar: 2 2 to 4 4
Total Qty | Total ΣD cable (mm) | Required common width (mm) | Recommended single ladder (mm) | Single width utilization % | Single width result | 2 2: Parallel ladders; 3 3: Width / parallel ladder (mm); 4 4: Recommendation
85 | 1240 | 1550 | MULTIPLE |  | MULTIPLE | 2 2: 2; 3 3: 1000; 4 4: 2 parallel ladders @ 1000 mm
Candidate ladder widths ¦ single-route and parallel-route screening | bar: 2 2
Nominal ladder width (mm) | 0.8W limit (mm) | Total ΣD cable (mm) | Single width utilization % | Single route result | Minimum parallel ladders | 2 2: Utilization after parallel %
200 | 160 | 1240 | 775% | FAIL | 8 | 2 2: 96.88%
300 | 240 | 1240 | 516.7% | FAIL | 6 | 2 2: 86.11%
400 | 320 | 1240 | 387.5% | FAIL | 4 | 2 2: 96.88%
500 | 400 | 1240 | 310% | FAIL | 4 | 2 2: 77.5%
600 | 480 | 1240 | 258.3% | FAIL | 3 | 2 2: 86.11%
700 | 560 | 1240 | 221.4% | FAIL | 3 | 2 2: 73.81%
800 | 640 | 1240 | 193.8% | FAIL | 2 | 2 2: 96.88%
900 | 720 | 1240 | 172.2% | FAIL | 2 | 2 2: 86.11%
1000 | 800 | 1240 | 155% | FAIL | 2 | 2 2: 77.5%

## 2.Ladder-Tray-(PV)
PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register | PV Ladder + Cable Tray Summary ¦ Jinko 725 Wp containment reference ¦ OD linked to Vendor Register
Combined view: ladder section and cable-tray section are both on this sheet. PV cable sizes 4/6/10/16 mm² use linked OD values from Vendor Register. | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง | วสท. 022001-22 ข้อ 5.15: สายแกนเดียวมีเปลือกที่วางตรงบน cable ladder ต้องมีขนาดตัวนำไม่น้อยกว่า 25 mm² ดังนั้น PV H1Z2Z2-K 4/6 mm² มีจำนวนที่อนุญาตให้วางตรง = 0 ทุกความกว้าง
For cable tray/ladder, do not treat the wireway 20% rule as direct permission. Confirm cable eligibility, usable width, support/load and the additional ΣD_cable ≤0.8W screen. | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก | แถว THEORETICAL PHYSICAL ONLY คำนวณจาก N = floor(W_nominal / (1.25 x OD)) เพื่อประเมินพื้นที่เท่านั้น ไม่ทำให้การวางตรงเป็นไปตาม วสท.; แนวทางใช้งานคือเดิน PV ใน IMC/ช่องเดินสายปิดที่เหมาะสม แล้วรองรับท่อบน ladder ตาม shop drawing และน้ำหนักบรรทุก
PV 1C Cable on Cable Ladder ¦ EIT eligibility and physical screening | Nominal ladder width (mm) - replace with actual usable width | Nominal ladder width (mm) - replace with actual usable width | Nominal ladder width (mm) - replace with actual usable width | Nominal ladder width (mm) - replace with actual usable width | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000
EIT working rule: PV single-core cable smaller than 25 mm² is not shown as direct-on-ladder. The theoretical count below is physical-only and not a direct installation permission. | CSA mm² | OD max mm | Direct-on-ladder eligibility | Count type | 200 mm | 300 mm | 400 mm | 500 mm | 600 mm | 700 mm | 800 mm | 900 mm | 1000 mm
Theoretical physical-only count uses N = floor(Wusable / (1.25 × OD)). Replace nominal/assumed width with confirmed usable width before design. | 4 | 6.2 | NOT PERMITTED DIRECT | DIRECT ALLOWABLE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nominal width (mm) — replace with confirmed usable width | 6 | 6.4 | NOT PERMITTED DIRECT | DIRECT ALLOWABLE | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000
PV cable | CSA mm² | OD linked mm | Direct eligibility | Count type | 200 mm | 300 mm | 400 mm | 500 mm | 600 mm | 700 mm | 800 mm | 900 mm | 1000 mm
Phelps Dodge H1Z2Z2-K | 4 | 6 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 6 | 7 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 10 | 8.2 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 16 | 9.8 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 4 | 6 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 26 | 40 | 53 | 66 | 80 | 93 | 106 | 120 | 133
Phelps Dodge H1Z2Z2-K | 6 | 7 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 22 | 34 | 45 | 57 | 68 | 80 | 91 | 102 | 114
Phelps Dodge H1Z2Z2-K | 10 | 8.2 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 19 | 29 | 39 | 48 | 58 | 68 | 78 | 87 | 97
Phelps Dodge H1Z2Z2-K | 16 | 9.8 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 16 | 24 | 32 | 40 | 48 | 57 | 65 | 73 | 81
PV 1C Cable on Cable Tray ¦ EIT eligibility and physical screening
EIT working rule: do not substitute wireway 20% fill for tray. Apply cable type eligibility, usable width, support/load and the additional ΣD_cable ≤0.8W width screen.
Theoretical physical-only count uses N = floor(Wusable / (1.25 × OD)). Replace nominal/assumed width with confirmed usable width before design.
Nominal width (mm) — replace with confirmed usable width |  |  |  |  | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000
PV cable | CSA mm² | OD linked mm | Direct eligibility | Count type | 200 mm | 300 mm | 400 mm | 500 mm | 600 mm | 700 mm | 800 mm | 900 mm | 1000 mm
Phelps Dodge H1Z2Z2-K | 4 | 6 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 6 | 7 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 10 | 8.2 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 16 | 9.8 | NOT PERMITTED DIRECT | DIRECT COUNT = 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phelps Dodge H1Z2Z2-K | 4 | 6 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 26 | 40 | 53 | 66 | 80 | 93 | 106 | 120 | 133
Phelps Dodge H1Z2Z2-K | 6 | 7 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 22 | 34 | 45 | 57 | 68 | 80 | 91 | 102 | 114
Phelps Dodge H1Z2Z2-K | 10 | 8.2 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 19 | 29 | 39 | 48 | 58 | 68 | 78 | 87 | 97
Phelps Dodge H1Z2Z2-K | 16 | 9.8 | NOT PERMITTED DIRECT | THEORETICAL PHYSICAL ONLY | 16 | 24 | 32 | 40 | 48 | 57 | 65 | 73 | 81
Ladder ¦ PV Cable Linked OD and Physical Screening | Ladder ¦ PV Cable Linked OD and Physical Screening | Ladder ¦ PV Cable Linked OD and Physical Screening | Ladder ¦ PV Cable Linked OD and Physical Screening | Ladder ¦ PV Cable Linked OD and Physical Screening | 19 16: Ladder ¦ PV Cable Linked OD and Physical Screening; 29 24: Ladder ¦ PV Cable Linked OD and Physical Screening; 39 32: Ladder ¦ PV Cable Linked OD and Physical Screening
PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing. | PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing. | PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing. | PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing. | PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing. | 19 16: PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing.; 29 24: PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing.; 39 32: PV single-core cables below 25 mm² are shown as NOT PERMITTED DIRECT on ladder under the current EIT working rule. The count is theoretical physical screening only; use protected route/closed channel and confirm shop drawing.
Cable ID | CSA (mm²) | OD linked (mm) | Direct eligibility | Width basis (mm) | 19 16: Theoretical / width max qty; 29 24: Width used at max (mm); 39 32: Width occupancy
PV-PD-4 | 4 | 6 | NOT PERMITTED DIRECT | 400 | 19 16: 53; 29 24: 318; 39 32: 79.5%
PV-PD-6 | 6 | 7 | NOT PERMITTED DIRECT | 400 | 19 16: 45; 29 24: 315; 39 32: 78.75%
PV-PD-10 | 10 | 8.2 | NOT PERMITTED DIRECT | 400 | 19 16: 39; 29 24: 319.8; 39 32: 79.95%
PV-PD-16 | 16 | 9.8 | NOT PERMITTED DIRECT | 400 | 19 16: 32; 29 24: 313.6; 39 32: 78.4%
Change the width basis in E5:E8 to the actual usable ladder width. Do not treat theoretical count as direct-on-ladder permission for PV 4/6/10/16 mm². | bar: 19 16 to 39 32
Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening | Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening | Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening | Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening | Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening | 19 16: Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening; 29 24: Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening; 39 32: Cable Tray ¦ PV Cable Linked OD and 0.8W Width Screening
Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement. | Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement. | Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement. | Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement. | Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement. | 19 16: Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement.; 29 24: Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement.; 39 32: Cable tray does not use the wireway 20% rule as a direct substitute. This view applies the requested extra width screen ΣD_cable ≤0.8W; confirm tray construction, usable width, support span and cable arrangement.
Cable ID | CSA (mm²) | OD linked (mm) | Direct eligibility | Width basis (mm) | 19 16: Theoretical / width max qty; 29 24: Width used at max (mm); 39 32: Width occupancy
PV-PD-4 | 4 | 6 | NOT PERMITTED DIRECT | 400 | 19 16: 53; 29 24: 318; 39 32: 79.5%
PV-PD-6 | 6 | 7 | NOT PERMITTED DIRECT | 400 | 19 16: 45; 29 24: 315; 39 32: 78.75%
PV-PD-10 | 10 | 8.2 | NOT PERMITTED DIRECT | 400 | 19 16: 39; 29 24: 319.8; 39 32: 79.95%
PV-PD-16 | 16 | 9.8 | NOT PERMITTED DIRECT | 400 | 19 16: 32; 29 24: 313.6; 39 32: 78.4%
Change the width basis in E5:E8 to the actual usable tray width. The 0.8W condition is a width arrangement screen and must be checked with actual cable grouping and support design. | bar: 19 16 to 39 32

## 3.PV Wireway
PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen | PV 1C Cable in Wireway ¦ EIT 20% Fill + requested ΣD_cable ≤0.8W screen
Rule basis: wireway cable area ≤20% of internal W×H. The extra width screen ΣD_cable ≤0.8W is shown separately and is not a replacement for the 20% area rule. OD values are linked to Vendor Register. | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN | วสท. 022001-22 ข้อ 5.12: ช่วงปกติ พื้นที่หน้าตัดรวมของสายรวมฉนวนต้องไม่เกิน 20% ของพื้นที่ภายใน wireway; ตารางนี้ใช้ internal W x H ตัวอย่างและ OD สูงสุดของ Prysmian PRYSUN
CCC >30 is a grouping/ampacity HOLD POINT. Confirm actual internal dimensions, cable OD, installation method, connector space, bending radius and support before final design. | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating | จุดต่อ/แยกที่เปิดตรวจได้อาจใช้เกณฑ์รวมสายและ connector ไม่เกิน 75% แต่ไม่ได้ใช้ในตารางนี้. ค่าเกิน 30 current-carrying conductors ไม่ใช่ข้อห้ามด้านพื้นที่ แต่เป็น HOLD POINT สำหรับ grouping/ampacity derating
Max String @20% area
Example internal size | W int. (mm) | H int. (mm) | Internal area (mm²) | 4 mm² max qty | 6 mm² max qty | 10 mm² max qty | 16 mm² max qty | CCC checkpoint | Engineering status |  |  |  | Wireway size | W (mm) | H (mm) | Internal area (mm²) | 4 mm² fill % | 6 mm² fill % | 10 mm² fill % | 16 mm² fill % | CCC checkpoint | Engineering status
50 x 50 mm | 50 | 50 | 2500 | 17 | 12 | 9 | 6 | <=30 CCC SCREEN | Screening only; confirm dimensions and apply 0.8W check below |  |  |  | 50 x 50 mm | 50 | 50 | 2500 | 19.23% | 18.47% | 19.01% | 18.1% | <=30 CCC SCREEN | Screening only; confirm dimensions and apply 0.8W check below
75 x 75 mm | 75 | 75 | 5625 | 39 | 29 | 21 | 14 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 75 x 75 mm | 75 | 75 | 5625 | 19.6% | 19.84% | 19.72% | 18.77% | DERATING CHECK >30 CCC | DERATING / grouping check required
100 x 50 mm | 100 | 50 | 5000 | 35 | 25 | 18 | 13 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 100 x 50 mm | 100 | 50 | 5000 | 19.79% | 19.24% | 19.01% | 19.61% | DERATING CHECK >30 CCC | DERATING / grouping check required
100 x 100 mm | 100 | 100 | 10000 | 70 | 51 | 37 | 26 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 100 x 100 mm | 100 | 100 | 10000 | 19.79% | 19.63% | 19.54% | 19.61% | DERATING CHECK >30 CCC | DERATING / grouping check required
150 x 100 mm | 150 | 100 | 15000 | 106 | 77 | 56 | 39 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 150 x 100 mm | 150 | 100 | 15000 | 19.98% | 19.76% | 19.72% | 19.61% | DERATING CHECK >30 CCC | DERATING / grouping check required
150 x 150 mm | 150 | 150 | 22500 | 159 | 116 | 85 | 59 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 150 x 150 mm | 150 | 150 | 22500 | 19.98% | 19.84% | 19.95% | 19.78% | DERATING CHECK >30 CCC | DERATING / grouping check required
200 x 100 mm | 200 | 100 | 20000 | 141 | 103 | 75 | 53 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 200 x 100 mm | 200 | 100 | 20000 | 19.93% | 19.82% | 19.8% | 19.99% | DERATING CHECK >30 CCC | DERATING / grouping check required
200 x 150 mm | 200 | 150 | 30000 | 212 | 155 | 113 | 79 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 200 x 150 mm | 200 | 150 | 30000 | 19.98% | 19.88% | 19.89% | 19.86% | DERATING CHECK >30 CCC | DERATING / grouping check required
200 x 200 mm | 200 | 200 | 40000 | 282 | 207 | 151 | 106 | DERATING CHECK >30 CCC | DERATING / grouping check required |  |  |  | 200 x 200 mm | 200 | 200 | 40000 | 19.93% | 19.92% | 19.94% | 19.99% | DERATING CHECK >30 CCC | DERATING / grouping check required
Fill ขนาดราง / ขนาดสาย / จำนวนสาย
PV Wireway detail ¦ area fill and additional 0.8W width condition
Each row can be changed for a project scenario. Area fill = Qty × πOD²/4 ÷ (W×H). Width utilization = Qty × OD ÷ W. Combined result requires both limits.
Scenario | W int. (mm) | H int. (mm) | Cable size (mm²) | OD linked (mm) | Qty input | ΣD cable (mm) | 0.8W limit (mm) | Width utilization % | Area fill % | 20% fill result | Combined result | CCC checkpoint
PV-WW-001 | 300 | 100 | 6 | 7 | 50 | 350 | 240 | 116.7% | 6.414% | PASS | CHECK | DERATING CHECK >30 CCC
PV-WW-002 | 300 | 100 | 6 | 7 | 100 | 700 | 240 | 233.3% | 12.83% | PASS | CHECK | DERATING CHECK >30 CCC
PV-WW-003 | 600 | 100 | 6 | 7 | 130 | 910 | 480 | 151.7% | 8.338% | PASS | CHECK | DERATING CHECK >30 CCC
PV-WW-004 | 100 | 100 | 16 | 9.8 | 6 | 58.8 | 80 | 58.8% | 4.526% | PASS | PASS | <=30 CCC SCREEN
PV-WW-005 | 150 | 100 | 16 | 9.8 | 50 | 490 | 120 | 326.7% | 25.14% | FAIL | CHECK | DERATING CHECK >30 CCC
กำหนดจากขนาดราง Wireway และดู MAX
Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen | Wireway ¦ PV Cable Linked OD, 20% Area Fill and 0.8W Width Screen
Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate. | Yellow cells are project dimensions and selected quantity. OD is linked to Vendor Register. PASS requires both wireway fill ≤20% and the additional width screen ΣD_cable ≤0.8W; CCC/grouping and thermal checks remain separate.
Input | Value
W internal (mm) | 300
H internal (mm) | 100
Area fill limit | 20%
Width factor | 80% | 0.8W
Cable ID | CSA (mm²) | OD linked (mm) | Area / cable (mm²) | Max qty @20% area | Max String @20% area | Max qty @0.8W | Max String @0.8W | CCC checkpoint | Selected qty | Area fill % | ΣD / W % | Combined status
PV-PD-4 | 4 | 6 | 28.2743 | 212 | 106 | 40 | 20 | DERATING CHECK >30 CCC | 10 | 0.9425% | 20% | PASS
PV-PD-6 | 6 | 7 | 38.4845 | 155 | 77 | 34 | 17 | DERATING CHECK >30 CCC | 4 | 0.5131% | 9.333% | PASS
PV-PD-10 | 10 | 8.2 | 52.8102 | 113 | 56 | 29 | 14 | <=30 CCC SCREEN | 4 | 0.7041% | 10.93% | PASS
PV-PD-16 | 16 | 9.8 | 75.4296 | 79 | 39 | 24 | 12 | <=30 CCC SCREEN | 2 | 0.5029% | 6.533% | PASS
Wireway selection summary ¦ lower-table inputs screened with ΣD cable ≤ 0.8W and 20% area fill
This table uses the selected Qty in J35:J38, linked OD in C35:C38 and area/cable in D35:D38. It evaluates the mixed cable total against each candidate W×H size.
Wireway size | W int. (mm) | H int. (mm) | Total selected Qty | Total ΣD cable (mm) | 0.8W limit (mm) | 0.8W utilization % | Total cable area (mm²) | Area fill % | 0.8W result | 20% fill result | Combined result | Recommendation
50 x 50 mm | 50 | 50 | 20 | 140.4 | 40 | 351% | 798.7813 | 31.95% | FAIL | FAIL | CHECK | Increase W / split route
75 x 75 mm | 75 | 75 | 20 | 140.4 | 60 | 234% | 798.7813 | 14.2% | FAIL | PASS | CHECK | Increase W / split route
100 x 50 mm | 100 | 50 | 20 | 140.4 | 80 | 175.5% | 798.7813 | 15.98% | FAIL | PASS | CHECK | Increase W / split route
100 x 100 mm | 100 | 100 | 20 | 140.4 | 80 | 175.5% | 798.7813 | 7.988% | FAIL | PASS | CHECK | Increase W / split route
150 x 100 mm | 150 | 100 | 20 | 140.4 | 120 | 117% | 798.7813 | 5.325% | FAIL | PASS | CHECK | Increase W / split route
150 x 150 mm | 150 | 150 | 20 | 140.4 | 120 | 117% | 798.7813 | 3.55% | FAIL | PASS | CHECK | Increase W / split route
200 x 100 mm | 200 | 100 | 20 | 140.4 | 160 | 87.75% | 798.7813 | 3.994% | PASS | PASS | PASS | USE
200 x 150 mm | 200 | 150 | 20 | 140.4 | 160 | 87.75% | 798.7813 | 2.663% | PASS | PASS | PASS | USE
200 x 200 mm | 200 | 200 | 20 | 140.4 | 160 | 87.75% | 798.7813 | 1.997% | PASS | PASS | PASS | USE

## Fill Check - EIT
Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required | Physical Fill Calculator - Project Inputs Required
Rev.4: select Cable type/model from the Phelps Dodge dropdown. OD is formula-linked to IMC Max Count!E10:E13. This calculator checks area fill only; no 0.8W condition is applied. Width occupied is informational. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied. | Yellow cells are project/manufacturer inputs. Result stays REVIEW until selected rule, limit and confirmed usable dimension are supplied.
|  |  |  | Cable type/model (Phelps Dodge dropdown) | Cable OD from IMC (mm) |  |  |  |  | Rule type (Area only) | [5 empty] | Width occupied (mm) — information | Width occupancy — information
Circuit ID | Containment type | Brand | Model | Cable type/model | Cable OD (mm) | No. cables | Arrangement | Confirmed ID / usable width (mm) | Confirmed usable depth (mm) | Rule type | Allowed fill / occupancy | Rule source | A_used (mm2) | A_internal (mm2) | Physical fill % | Width occupied (mm) | Width occupancy % | Thermal check status | Result | Remark
CIR-EX-001 | Wireway | Phelps Dodge | WW-100x100 | Phelps Dodge H1Z2Z2-K 4 mm² | 6 | 40 | area fill screening | 100 | 100 | Area | 20% | WST 022001-22 cl.5.12 / EIT-WW-01 | 1130.9734 | 10000 | 11.31% | 240 | 240% | PASS | PASS | Example 1: 4 mm², 40 cables; area-only
CIR-EX-002 | Wireway | Phelps Dodge | WW-200x100 | Phelps Dodge H1Z2Z2-K 6 mm² | 7 | 55 | area fill screening | 200 | 100 | Area | 20% | WST 022001-22 cl.5.12 / EIT-WW-01 | 2116.6481 | 20000 | 10.58% | 385 | 192.5% | PASS | PASS | Example 2: 6 mm², 55 cables; area-only
CIR-EX-003 | Wireway | Phelps Dodge | WW-100x100 | Phelps Dodge H1Z2Z2-K 10 mm² | 8.2 | 40 | area fill screening | 100 | 100 | Area | 20% | WST 022001-22 cl.5.12 / EIT-WW-01 | 2112.4069 | 10000 | 21.12% | 328 | 328% | PASS | FAIL | Example 3: 10 mm², 40 cables intentionally above 20%
CIR-004 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-005 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-006 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-007 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-008 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-009 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-010 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-011 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-012 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-013 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-014 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-015 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-016 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-017 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-018 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-019 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW
CIR-020 | [9 empty] | Area | 20% | [6 empty] | OPEN | REVIEW

## Source Register
Source Register and Review Status | Source Register and Review Status | Source Register and Review Status | Source Register and Review Status | Source Register and Review Status | Source Register and Review Status | Source Register and Review Status | Source Register and Review Status
Source ID | Manufacturer | Document | Local file | Official URL | Pages used | SHA-256 | Status / limitation
SRC-EIT-001 | EIT | Electrical Installation Standard Thailand 2564 - official sample/TOC | Standards/EIT_022001-22_2564_Official_Sample_TOC.pdf | https://eit.or.th/api/public/file/book/66 | TOC: 5.12 wireways; 5.15 cable trays | F97BBF385AD3F264C8D9A710B143960531EE626CD44A821E4AA2D932B7355B90 | Confirms edition and clause locations; use licensed full standard for final design.
SRC-CAB-001 | Bangkok Cable | Electrical Design & Installation Guide, Revised Third Edition | Datasheet/Bangkok_Cable_Electrical_Design_Installation_Guide.pdf | https://www.bangkokcable.com/ | PDF 149-150, 240-242, 383-387, 431 | 407AA9AAC9CC7F130B1F0DEDDB010561769EEEF85413FE22C4339D61A46960FC | EIT-based conduit fill, tray eligibility/arrangement and screening width rule.
SRC-CON-001 | Panasonic SPT (Thailand) | White Conduit & Conduit Fittings catalogue | Datasheet/Panasonic_White_Conduit_Catalogue.pdf | https://lssth.panasonic.com/download/ecm/conduit_pipe/pdf/White-Conduit.pdf | PDF 5 | EAC580225D7CF090AAB84AB2FDFDEDE2E1095BD0BCA6678925D9743EB127D219 | OD/min wall only; calculated internal ID is screening, not certified actual ID.
SRC-LAD-001 | KJL | KJL Catalogue 2022-2023 - KLSG Cable Ladder | Datasheet/KJL_Catalogue_Cable_Ladder.pdf | https://kjl.co.th/product/cable-systems/cable-ladder/ | PDF 122-125 | 4EF6DB535BF779196E858254D88F2AEAAC4AE80104E1FEDEC043ACE24991DD07 | Nominal width used; confirm usable width, supports and current shop drawing.
SRC-PV-001 | Prysmian | PRYSUN H1Z2Z2-K datasheet | Datasheet/Vendor_Reference/Prysmian_PRYSUN_H1Z2Z2-K_Datasheet.pdf | https://www.prysmian.com/ | PDF 2-3 | 23787892DE273577BE7AB3209300C689481AB5D273E160B0511DF07CB26DFE37 | Maximum OD used for 1C 4/6 mm² PV physical screening.
SRC-AC-001 | Phelps Dodge | Low Voltage Power and Control Cables - CV family | Datasheet/Vendor_Reference/Phelps_Dodge_LV_Power_Control_Cables.pdf | https://www.pdcable.com/product/cv-fd-1/ | PDF 11, 14, 17, 20 | 01507A7209398B3D4347302A933F8CCBCB1CACC25253D96D9615992923E4338C | Approximate CV OD used as reference; exact CV-FD code/revision OD mandatory.